## Instantaneous Values
Instantaneous Values | Adress | Multiplier | Unit | Type | W/R
Current and Power Precision (Modbus) | 10026 | 1 | - | int 32 | R
Current Transformer Ratio | 10028 | 1 | - | int 32 | R
Nominal Line Voltage | 10030 | 1 | V | int 32 | R
Nominal Measuring Voltage | 10032 | 1 | V | int 32 | R
Temperature 1 | 10036 | 0.1 | Celcius | int 32 | R
Device Internal Supply Voltage | 10042 | 1 | Volt | int 32 | R
Battery Voltage | 10044 | 0.001 | Volt | int 32 | R
Date / Time (UTC) | 10046 | 1 | Timestamp | int 32 | R
Serial Number | 10048 | 1 | - | int 32 | R
1. Phase-Neutral Voltage | 10050 | 0.1 | Volt | int 32 | R
2. Phase-Neutral Voltage | 10052 | 0.1 | Volt | int 32 | R
3. Phase-Neutral Voltage | 10054 | 0.1 | Volt | int 32 | R
L1-L2 Line-to-Line Voltage | 10058 | 0.1 | Volt | int 32 | R
L2-L3 Line-to-Line Voltage | 10060 | 0.1 | Volt | int 32 | R
L3-L1 Line-to-Line Voltage | 10062 | 0.1 | Volt | int 32 | R
1. Phase Current | 10064 | 0.001 | Ampere | int 32 | R
2. Phase Current | 10066 | 0.001 | Ampere | int 32 | R
3. Phase Current | 10068 | 0.001 | Ampere | int 32 | R
Neutral Current | 10070 | 0.001 | Ampere | int 32 | R
1.Phase Active Power | 10072 | 1 | Watt | int 32 | R
2.Phase Active Power | 10074 | 1 | Watt | int 32 | R
3.Phase Active Power | 10076 | 1 | Watt | int 32 | R
1.Phase Reactive Power | 10078 | 1 | VAr | int 32 | R
2.Phase Reactive Power | 10080 | 1 | VAr | int 32 | R
3.Phase Reactive Power | 10082 | 1 | VAr | int 32 | R
1.Phase Apparent Power | 10084 | 1 | VA | int 32 | R
2.Phase Apparent Power | 10086 | 1 | VA | int 32 | R
3.Phase Apparent Power | 10088 | 1 | VA | int 32 | R
1. Phase Frequency | 10090 | 0.01 | Hz | int 32 | R
2. Phase Frequency | 10092 | 0.01 | Hz | int 32 | R
3. Phase Frequency | 10094 | 0.01 | Hz | int 32 | R
1. Phase cos(fi) | 10096 | 0.001 | - | int 32 | R
2. Phase cos(fi) | 10098 | 0.001 | - | int 32 | R
3. Phase cos(fi) | 10100 | 0.001 | - | int 32 | R
1. Phase tan(fi) | 10102 | 0.001 | - | int 32 | R
2. Phase tan(fi) | 10104 | 0.001 | - | int 32 | R
3. Phase tan(fi) | 10106 | 0.001 | - | int 32 | R
1. Phase PF | 10108 | 0.001 | - | int 32 | R
2. Phase PF | 10110 | 0.001 | - | int 32 | R
3. Phase PF | 10112 | 0.001 | - | int 32 | R
1. Phase THVD | 10114 | 0.1 | % | int 32 | R
2. Phase THVD | 10116 | 0.1 | % | int 32 | R
3. Phase THVD | 10118 | 0.1 | % | int 32 | R
1. Phase THID | 10120 | 0.1 | % | int 32 | R
2. Phase THID | 10122 | 0.1 | % | int 32 | R
3. Phase THID | 10124 | 0.1 | % | int 32 | R
1.Phase Current Fundamental Component | 10150 | 0.001 | Ampere | int 32 | R
2.Phase Current Fundamental Component | 10152 | 0.001 | Ampere | int 32 | R
3.Phase Current Fundamental Component | 10154 | 0.001 | Ampere | int 32 | R
1.Phase Voltage Fundamental Component | 10156 | 0.1 | Volt | int 32 | R
2.Phase Voltage Fundamental Component | 10158 | 0.1 | Volt | int 32 | R
3.Phase Voltage Fundamental Component | 10160 | 0.1 | Volt | int 32 | R
1.Phase Active Power Fundamental Component | 10162 | 1 | Watt | int 32 | R
2.Phase Active Power Fundamental Component | 10164 | 1 | Watt | int 32 | R
3.Phase Active Power Fundamental Component | 10166 | 1 | Watt | int 32 | R
1.Phase Reactive Power Fundamental Component | 10168 | 1 | VAr | int 32 | R
2.Phase Reactive Power Fundamental Component | 10170 | 1 | VAr | int 32 | R
3.Phase Reactive Power Fundamental Component | 10172 | 1 | VAr | int 32 | R
Voltage Angle(L1-L1) | 10180 | 1 | Degree | int 32 | R
Voltage Angle(L1-L2) | 10182 | 1 | Degree | int 32 | R
Voltage Angle(L1-L3) | 10184 | 1 | Degree | int 32 | R
1.Phase Current Angle | 10186 | 1 | Degree | int 32 | R
2.Phase Current Angle | 10188 | 1 | Degree | int 32 | R
3.Phase Current Angle | 10190 | 1 | Degree | int 32 | R
1.Phase Voltage Current Angle Difference | 10192 | 1 | Degree | int 32 | R
2.Phase Voltage Current Angle Difference | 10194 | 1 | Degree | int 32 | R
3.Phase Voltage Current Angle Difference | 10196 | 1 | Degree | int 32 | R
Voltage Angle Difference(L1-L2) | 10198 | 1 | Degree | int 32 | R
Voltage Angle Difference(L2-L3) | 10200 | 1 | Degree | int 32 | R
Voltage Angle Difference(L1-L3) | 10202 | 1 | Degree | int 32 | R
Current Angle Difference(L1-L2) | 10204 | 1 | Degree | int 32 | R
Current Angle Difference(L2-L3) | 10206 | 1 | Degree | int 32 | R
Current Angle Difference(L1-L3) | 10208 | 1 | Degree | int 32 | R
Voltage Unbalance(%) | 10210 | 0.1 | - | int 32 | R
Current Unbalance(%) | 10212 | 0.1 | - | int 32 | R
Input-1 Edge Trigger Count | 10230 | 1 | - | uint32 | R
Input-1 Edge Trigger Unit Energy Count | 10232 | 1 | - | uint32 | R
Input-1 Pulse Count | 10234 | 1 | - | uint32 | R
Input-1 Pulse Unit Energy Number | 10236 | 1 | - | uint32 | R
Input-2 Edge Trigger Count | 10238 | 1 | - | uint32 | R
Input-2 Edge Trigger Unit Energy Count | 10240 | 1 | - | uint32 | R
Input-2 Pulse Count | 10242 | 1 | - | uint32 | R
Input-2 Pulse Unit Energy Number | 10244 | 1 | - | uint32 | R

## Instantaneous Peak Values (Cons
Instantaneous Peak Values (Consumption) | Adress | Multiplier | Unit | Type | W/R
1. Phase Min Voltage (L-N) | 11010 | 0.1 | V(Volt) | int32 | R
2. Phase Min Voltage (L-N) | 11012 | 0.1 | V(Volt) | int32 | R
3. Phase Min Voltage (L-N) | 11014 | 0.1 | V(Volt) | int32 | R
Neutral Min Voltage | 11016 | 0.1 | V(Volt) | int32 | R
1. Phase Max Voltage (L-N) | 11018 | 0.1 | V(Volt) | int32 | R
2. Phase Max Voltage (L-N) | 11020 | 0.1 | V(Volt) | int32 | R
3. Phase Max Voltage (L-N) | 11022 | 0.1 | V(Volt) | int32 | R
Neutral Max Voltage | 11024 | 0.1 | V(Volt) | int32 | R
1. Phase Min Voltage (L12) | 11026 | 0.1 | V(Volt) | int32 | R
2. Phase Min Voltage (L23) | 11028 | 0.1 | V(Volt) | int32 | R
3. Phase Min Voltage (L31) | 11030 | 0.1 | V(Volt) | int32 | R
1. Phase Max Voltage (L12) | 11032 | 0.1 | V(Volt) | int32 | R
2. Phase Max Voltage (L23) | 11034 | 0.1 | V(Volt) | int32 | R
3. Phase Max Voltage (L31) | 11036 | 0.1 | V(Volt) | int32 | R
1. Phase Min Current (Import) | 11038 | 1 | A(Ampere) | int32 | R
2. Phase Min Current (Import) | 11040 | 1 | A(Ampere) | int32 | R
3. Phase Min Current (Import) | 11042 | 1 | A(Ampere) | int32 | R
Neutral Min Current | 11044 | 1 | A(Ampere) | int32 | R
1. Phase Max Current | 11046 | 1 | A(Ampere) | int32 | R
2. Phase Max Current | 11048 | 1 | A(Ampere) | int32 | R
3. Phase Max Current | 11050 | 1 | A(Ampere) | int32 | R
Neutral Max Current | 11052 | 1 | A(Ampere) | int32 | R
1. Phase Min Active Power (Import) | 11054 | 1 | P(Watt) | int32 | R
2. Phase Min Active Power (Import) | 11056 | 1 | P(Watt) | int32 | R
3. Phase Min Active Power (Import) | 11058 | 1 | P(Watt) | int32 | R
1. Phase Max Active Power | 11060 | 1 | P(Watt) | int32 | R
2. Phase Max Active Power | 11062 | 1 | P(Watt) | int32 | R
3. Phase Max Active Power | 11064 | 1 | P(Watt) | int32 | R
1. Phase Min Reactive Power | 11066 | 1 | Q(VAR) | int32 | R
2. Phase Min Reactive Power | 11068 | 1 | Q(VAR) | int32 | R
3. Phase Min Reactive Power | 11070 | 1 | Q(VAR) | int32 | R
1. Phase Max Reactive Power | 11072 | 1 | Q(VAR) | int32 | R
2. Phase Max Reactive Power | 11074 | 1 | Q(VAR) | int32 | R
3. Phase Max Reactive Power | 11076 | 1 | Q(VAR) | int32 | R
1. Phase Min Apparent Power | 11078 | 1 | S(VA) | int32 | R
2. Phase Min Apparent Power | 11080 | 1 | S(VA) | int32 | R
3. Phase Min Apparent Power | 11082 | 1 | S(VA) | int32 | R
1. Phase Max Apparent Power | 11084 | 1 | S(VA) | int32 | R
2. Phase Max Apparent Power | 11086 | 1 | S(VA) | int32 | R
3. Phase Max Apparent Power | 11088 | 1 | S(VA) | int32 | R
1. Phase Min THVD | 11100 | 0.1 | % | int32 | R
2. Phase Min THVD | 11102 | 0.1 | % | int32 | R
3. Phase Min THVD | 11104 | 0.1 | % | int32 | R
1. Phase Max THVD | 11106 | 0.1 | % | int32 | R
2. Phase Max THVD | 11108 | 0.1 | % | int32 | R
3. Phase Max THVD | 11110 | 0.1 | % | int32 | R
1. Phase Min THID | 11112 | 0.1 | % | int32 | R
2. Phase Min THID | 11114 | 0.1 | % | int32 | R
3. Phase Min THID | 11116 | 0.1 | % | int32 | R
1. Phase MaxTHID | 11118 | 0.1 | % | int32 | R
2. Phase MaxTHID | 11120 | 0.1 | % | int32 | R
3. Phase Max THID | 11122 | 0.1 | % | int32 | R
Min Frequency | 11136 | 0.01 | Hz | int32 | R
Max Frequency | 11138 | 0.01 | Hz | int32 | R
Min Voltage Unbalance | 11140 | - | % | int32 | R
Max Voltage Unbalance | 11142 | - | % | int32 | R
Min Current Unbalance | 11144 | - | % | int32 | R
Max Current Unbalance | 11146 | - | % | int32 | R
Instantaneous Peak Values (Generation) | Adress | Multiplier | Unit | Type | W/R
1. Phase Min Voltage (L-N) | 11260 | 0.1 | V(Volt) | int32 | R
2. Phase Min Voltage (L-N) | 11262 | 0.1 | V(Volt) | int32 | R
3. Phase Min Voltage (L-N) | 11264 | 0.1 | V(Volt) | int32 | R
Neutral Min Voltage | 11266 | 0.1 |  | int32 | R
1. Phase Max Voltage (L-N) | 11268 | 0.1 | V(Volt) | int32 | R
2. Phase Max Voltage (L-N) | 11270 | 0.1 | V(Volt) | int32 | R
3. Phase Max Voltage (L-N) | 11272 | 0.1 | V(Volt) | int32 | R
Neutral Max Voltage | 11274 | 0.1 | V(Volt) | int32 | R
1. Phase Min Voltage (L12) | 11276 | 0.1 | V(Volt) | int32 | R
2. Phase Min Voltage (L23) | 11278 | 0.1 | V(Volt) | int32 | R
3. Phase Min Voltage (L31) | 11280 | 0.1 | V(Volt) | int32 | R
1. Phase Max Voltage (L12) | 11282 | 0.1 | V(Volt) | int32 | R
2. Phase Max Voltage (L23) | 11284 | 0.1 | V(Volt) | int32 | R
3. Phase Max Voltage (L31) | 11286 | 0.1 | V(Volt) | int32 | R
1. Phase Min Current (Import) | 11288 | 1 | A(Ampere) | int32 | R
2. Phase Min Current (Import) | 11290 | 1 | A(Ampere) | int32 | R
3. Phase Min Current (Import) | 11292 | 1 | A(Ampere) | int32 | R
Neutral Min Current | 11294 | 1 |  | int32 | R
1. Phase Max Current | 11296 | 1 | A(Ampere) | int32 | R
2. Phase Max Current | 11298 | 1 | A(Ampere) | int32 | R
3. Phase Max Current | 11300 | 1 | A(Ampere) | int32 | R
Neutral Max Current | 11302 | 1 |  | int32 | R
1. Phase Min Active Power (Import) | 11304 | 1 | P(Watt) | int32 | R
2. Phase Min Active Power (Import) | 11306 | 1 | P(Watt) | int32 | R
3. Phase Min Active Power (Import) | 11308 | 1 | P(Watt) | int32 | R
1. Phase Max Active Power | 11310 | 1 | P(Watt) | int32 | R
2. Phase Max Active Power | 11312 | 1 | P(Watt) | int32 | R
3. Phase Max Active Power | 11314 | 1 | P(Watt) | int32 | R
1. Phase Min Reactive Power | 11316 | 1 | Q(VAR) | int32 | R
2. Phase Min Reactive Power | 11318 | 1 | Q(VAR) | int32 | R
3. Phase Min Reactive Power | 11320 | 1 | Q(VAR) | int32 | R
1. Phase Max Reactive Power | 11322 | 1 | Q(VAR) | int32 | R
2. Phase Max Reactive Power | 11324 | 1 | Q(VAR) | int32 | R
3. Phase Max Reactive Power | 11326 | 1 | Q(VAR) | int32 | R
1. Phase Min Apparent Power | 11328 | 1 | S(VA) | int32 | R
2. Phase Min Apparent Power | 11330 | 1 | S(VA) | int32 | R
3. Phase Min Apparent Power | 11332 | 1 | S(VA) | int32 | R
1. Phase Max Apparent Power | 11334 | 1 | S(VA) | int32 | R
2. Phase Max Apparent Power | 11336 | 1 | S(VA) | int32 | R
3. Phase Max Apparent Power | 11338 | 1 | S(VA) | int32 | R
1. Phase Min THVD | 11350 | 0.1 | % | int32 | R
2. Phase Min THVD | 11352 | 0.1 | % | int32 | R
3. Phase Min THVD | 11354 | 0.1 | % | int32 | R
1. Phase Max THVD | 11356 | 0.1 | % | int32 | R
2. Phase Max THVD | 11358 | 0.1 | % | int32 | R
3. Phase Max THVD | 11360 | 0.1 | % | int32 | R
1. Phase Min THID | 11362 | 0.1 | % | int32 | R
2. Phase Min THID | 11364 | 0.1 | % | int32 | R
3. Phase Min THID | 11366 | 0.1 | % | int32 | R
1. Phase MaxTHID | 11368 | 0.1 | % | int32 | R
2. Phase MaxTHID | 11370 | 0.1 | % | int32 | R
3. Phase Max THID | 11372 | 0.1 | % | int32 | R
Min Frequency | 11386 | 0.01 | Hz | int32 | R
Max Frequency | 11388 | 0.01 | Hz | int32 | R
Min Voltage Unbalance | 11390 | - | % | int32 | R
Max Voltage Unbalance | 11392 | - | % | int32 | R
Min Current Unbalance | 11394 | - | % | int32 | R
Max Current Unbalance | 11396 | - | % | int32 | R

## Total, and Average Values
Total, and Average Values | Adress | Multiplier | Unit | Type | W/R
Total Active Power (Import) | 10410 | 1 | Watt | int 32 | R
Total Reactive Power (Import) | 10412 | 1 | VAr | int 32 | R
Total Inductive Power (Import) | 10414 | 1 | VAr | int 32 | R
Total Capacitive Power (Import) | 10416 | 1 | VAr | int 32 | R
Total Apparent Power (Import) | 10418 | 1 | VA | int 32 | R
Total Active Power (Export/Generation) | 10430 | 1 | Watt | int 32 | R
Total Reactive Power (Export/Generation) | 10432 | 1 | VAr | int 32 | R
Total Inductive Power (Export/Generation) | 10434 | 1 | VAr | int 32 | R
Total Capacitive Power (Export/Generation) | 10436 | 1 | VAr | int 32 | R
Total Apparent Power (Export/Generation) | 10438 | 1 | VA | int 32 | R
Average Current (Import) | 10452 | 1 | Ampere | int 32 | R
Average Active Power (Import) | 10454 | 1 | Watt | int 32 | R
Average Cos (Import) | 10456 | 1 | - | int 32 | R
Average Tan (Import) | 10458 | 0.1 | - | int 32 | R
Average Power Factor (Import) | 10460 | - | - | int 32 | R
Average Current (Export) | 10472 | 1 | Ampere | int 32 | R
Average Active Power (Export) | 10474 | 1 | Watt | int 32 | R
Average Cos (Export) | 10476 | 1 | - | int 32 | R
Average Tan (Export) | 10478 | 0.1 | - | int 32 | R
Average Power Factor (Export) | 10480 | - | - | int 32 | R
Average Voltage (L-N) | 10492 | 0.1 | Volt | int 32 | R
Average Voltage (L-L) | 10494 | 0.1 | Volt | int 32 | R
Average Frequency | 10496 | 0.01 | Hz | int 32 | R
Average THID | 10498 | 0.1 | - | int 32 | R
Average THVD | 10500 | 0.1 | - | int 32 | R

## Parameters
Parameter | Adress | W/R | Type | Unit | Min | Max | Default | Step | Table-1.0 |  | Table-2.2
Parameter Version | 200 | R | Uint 16 | - | 0 | 255 | 6 | - | Index | Modbus Speed | Index | Measurement Voltage (LN / LL)
Operating Time | 201 | R | Uint 16 | - | 0 | 32767 | 0 | - | 0 | 4800 bps | 0 | 13 / 22
Reset Status | 202 | R | Uint 16 | - | 0 | 1 | 0 | - | 1 | 9600 bps | 1 | 14 / 25
Power Down Counter | 203 | R | Uint 16 | - | 0 | 32767 | 0 | - | 2 | 19200 bps | 2 | 17 / 30
Modbus Address | 206 | W/R | Uint 16 | - | 1 | 247 | 1 | 1 | 3 | 38400 bps | 3 | 19 / 33
Modbus Speed (Table-1.0) | 210 | W/R | Uint 16 | bps | 0 | 5 | 1 | 1 | 4 | 57600 bps | 4 | 21 / 36
Read Protection Bit | 214 | R | Uint 16 | - | 0 | 1 | 0 | 1 | 5 | 115200 bps | 5 | 23 / 40
Write Protection Bit | 215 | R | Uint 16 | - | 0 | 1 | 0 | 1 | 6 | 256000 bps | 6 | 30 / 50
Read Password Acknowledge | 216 | W/R | Uint 16 | - |  |  | 0 | 1 |  |  | 7 | 35 / 60
Write Password Acknowledge | 217 | W/R | Uint 16 | - |  |  | 0 | 1 | Table-1.1 |  | 8 | 40 / 70
Current Transformer Ratio(Table-2.0)* | 221 | W/R | Uint 16 | - | 0 | 69 | 13 | 1 | Index | Modbus Mode | 9 | 45 / 80
Line Voltage(Table-2.1)* | 222 | W/R | Uint 16 | Volt | 0 | 57 | 12 | 1 | 0 | RTU | 10 | 50 / 90
Measuring Voltage(Table-2.2) * | 223 | W/R | Uint 16 | Volt | 0 | 37 | 22 | 1 | 1 | ASCII | 11 | 60 / 100
Demand Period | 226 | W/R | Uint 16 | - | 1 | 60 | 15 | 1 |  |  | 12 | 65 / 110
Modbus Current Resolution | 227 | W/R | Uint 16 | - | 1 | 1000 | 1 | 1 | Table-1.2 |  | 13 | 70 / 120
Reset - Unknown | 240 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | Index | Parity Setting | 14 | 100 / 173
Reset - Power On | 241 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | 0 | None | 15 | 110 / 190
Reset - Brown Out | 242 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | 1 | Odd | 16 | 115 / 200
Reset - WatchDog Timer | 243 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | 2 | Even | 17 | 120 / 208
Reset - Software Reset | 244 | R | Uint 16 | - | 0 | 65535 | 0 | 1 |  |  | 18 | 130 / 200
Reset - MCLR | 245 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | Table-2.0 |  | 19 | 135 / 230
Reset - Option Byte Loader | 246 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | Index | C. Transformer Ratio | 20 | 140 / 240
Reset - V1.8 Power | 247 | R | Uint 16 | - | 0 | 65535 | 0 | 1 | 0 | 5 / 5 | 21 | 220 / 380
Time Zone (GMT) | 249 | W/R | int_16 | - | -12 | 12 | 3 | 1 | 1 | 10 / 5 | 22 | 230 / 400
Date Time Timestamp (High) | 250 | W/R | Uint 16 | - | 0 | 65535 | 0 | 1 | 2 | 15 / 5 | 23 | 240 / 415
Date Time Timestamp (Low) | 251 | W/R | Uint_16 | - | 0 | 65535 | 0 | 1 | 3 | 20 / 5 | 24 | 255 / 440
Display Sample Count | 252 | W/R | Uint_16 | - | 1 | 16 | 8 | 1 | 4 | 25 / 5 | 25 | 265 / 460
Display Percentage Difference | 253 | W/R | Uint_16 | % | 5 | 50 | 30 | 1 | 5 | 30 / 5 | 26 | 280 / 480
Display Refresh Interval | 254 | W/R | Uint_16 | ms | 3 | 10 | 3 | 100 | 6 | 40 / 5 | 27 | 290 / 500
Enabling Display Information Messages | 255 | W/R | Uint_16 | - | 0 | 1 | 1 | - | 7 | 50 / 5 | 28 | 300 / 525
Enable Screen Saver | 256 | W/R | Uint_16 | - | 0 | 1 | 1 | - | 8 | 60 / 5 | 29 | 320 / 550
Screen Saver Delay Time | 257 | W/R | Uint_16 | dk | 2 | 180 | 30 | 1 | 9 | 70 / 5 | 30 | 345 / 600
Display Brightness Level | 258 | W/R | Uint_16 | % | 5 | 100 | 94 | 1 | 10 | 75 / 5 | 31 | 375 / 650
Language | 260 | W/R | Uint_16 | - | 0 | 1 | 0 | - | 11 | 80 / 5 | 32 | 400 / 690
Access Control Enable(Table-3) | 261 | W/R | Uint_16 | - | 0 | 2 | 0 | - | 12 | 90 / 5 | 33 | 420 / 725
Access Control Enable | 262 | W/R | Uint_16 | - | 0 | 1 | 0 | - | 13 | 100 / 5 | 34 | 460 / 800
Harmonic Profile(Table-4.0) | 265 | W/R | Uint_16 | - | 0 | 9 | 3 | - | 14 | 120 / 5 | 35 | 490 / 850
Harmonic Limit | 266 | W/R | Uint_16 | - | 7 | 63 | 31 | - | 15 | 125 / 5 | 36 | 520 / 900
Harmonic Analysis(Table-4.1) | 267 | W/R | Uint_16 | - | 0 | 2 | 0 | - | 16 | 130 / 5 | 37 | 575 / 1000
SD Card Used Space (%) | 270 | R | Uint_16 | % | 0 | 100 | 0 | 1 | 17 | 150 / 5
SD Card Periodic Recording Status | 271 | R | Uint_16 | - | 0 | 1 | 0 | - | 18 | 160 / 5 | Table-3
SD Card Recording Period | 272 | W/R | Uint_16 | ms | 1 | 150 | 5 | 200 | 19 | 175 / 5 | Index | Access Level
SD Card Recording Write Mode (Table-5.0) | 273 | W/R | Uint_16 | - | 0 | 1 | 1 | 1 | 20 | 180 / 5 | 0 | User
SD Card Recording Schedule (Table-5.1) | 274 | W/R | Uint_16 | - | 0 | 1 | 0 | 1 | 21 | 200 / 5 | 1 | Operator
SD Card Total Recording Duration Unit (Table-5.2) | 275 | W/R | Uint_16 | - | 0 | 4 | 4 | 1 | 22 | 225 / 5 | 2 | Expert
SD Card Total Recording Duration Value | 276 | W/R | Uint_16 | - | 0 | 250 | 0 | 1 | 23 | 240 / 5
SD Card Recordable Size/Magnitude (Table-5.3) | 277 | W/R | Uint_16 | - | 0 | 2 | 0 | 1 | 24 | 250 / 5 | Table-4.0
SD Card Daily Recording Mode | 278 | W/R | Uint_16 | - | 0 | 1 | 0 | - | 25 | 300 / 5 | Index | Harmonic Profile
SD Card File Size Limit | 279 | W/R | Uint_16 | mb | 1 | 100 | 10 | 1 | 26 | 330 / 5 | 0 | 1-13 Single
SD Card Folder Size Limit | 280 | W/R | Uint_16 | mb | 10 | 1000 | 100 | 1 | 27 | 350 / 5 | 1 | 1-13 Even
SD Card Recording Format (Table-5.4) | 281 | W/R | Uint_16 | - | 0 | 1 | 0 | 1 | 28 | 360 / 5 | 2 | 1-13 All
SD Card Recording Scheduling Duration Unit (Table-5.2) | 282 | W/R | Uint_16 | - | 0 | 4 | 4 | 1 | 29 | 400 / 5 | 3 | 1-31 Single
SD Card Recording Scheduling Duration Value | 283 | W/R | Uint_16 | - | 0 | 250 | 0 | 1 | 30 | 450 / 5 | 4 | 1-31 Even
USB Used Space (%) | 290 | R | Uint_16 | % | 0 | 100 | 0 | 1 | 31 | 500 / 5 | 5 | 1-31 All
USB Periodic Recording Status | 291 | R | Uint_16 | - | 0 | 1 | 0 | - | 32 | 520 / 5 | 6 | 1-63 Single
USB Recording Period | 292 | W/R | Uint_16 | ms | 200 | 30000 | 1000 | 200 | 33 | 550 / 5 | 7 | 1-63 Even
USB Recording Write Mode (Table-5.0) | 293 | W/R | Uint_16 | - | 0 | 1 | 1 | 1 | 34 | 600 / 5 | 8 | All Harmonics
USB Recording Schedule (Table-5.1) | 294 | W/R | Uint_16 | - | 0 | 1 | 0 | 1 | 35 | 630 / 5 | 9 | Custom Profile
USB Total Recording Duration Unit (Table-5.2) | 295 | W/R | Uint_16 | - | 0 | 4 | 4 | 1 | 36 | 650 / 5
USB Total Recording Duration Value | 296 | W/R | Uint_16 | - | 0 | 250 | 0 | 1 | 37 | 700 / 5 | Table-4.1
USB Recordable Size/Magnitude (Table-5.3) | 297 | W/R | Uint_16 | - | 0 | 2 | 0 | 1 | 38 | 730 / 5 | Index | Harmonic Type
USB Daily Recording Mode | 298 | W/R | Uint_16 | - | 0 | 1 | 0 | - | 39 | 750 / 5 | 0 | Single
USB File Size Limit | 299 | W/R | Uint_16 | mb | 1 | 100 | 10 | 1 | 40 | 800 / 5 | 1 | Even
USB Folder Size Limit | 300 | W/R | Uint_16 | mb | 10 | 1000 | 100 | 1 | 41 | 900 / 5 | 2 | All
USB Recording Format (Table-5.4) | 301 | W/R | Uint_16 | - | 0 | 1 | 0 | 1 | 42 | 1000 / 5
USB Recording Scheduling Duration Unit (Table-5.2) | 302 | W/R | Uint_16 | - | 0 | 4 | 4 | 1 | 43 | 1100 / 5 | Table-5.0
USB Recording Scheduling Duration Value | 303 | W/R | Uint_16 | - | 0 | 250 | 0 | 1 | 44 | 1200 / 5 | Index | Writing Style
Output Type (Table-6.0) | 309 | W/R | Uint_16 | - | 0 | 2 | 0 | 1 | 45 | 1250 / 5 | 0 | Cyclical
Output 1 Magnitude Type (Table-6.1) | 310 | W/R | Uint_16 | - | 0 | 10 | 0 | 1 | 46 | 1400 / 5 | 1 | Until Memory Ful
Output 1 Phase Selection (Table-6.2) | 311 | W/R | Uint_16 | - | 0 | 4 | 1 | 1 | 47 | 1500 / 5
Output 1 Inversion / Reversal | 312 | W/R | Uint_16 | - | 0 | 1 | 0 | - | 48 | 1600 / 5 | Table-5.1
Output 1 Upper Limit Value | 313 | W/R | Uint_16 | - | -9999 | 9999 | 2 | 1 | 49 | 1800 / 5 | Index | Write Schedule
Output 1 Lower Limit Value | 314 | W/R | Uint_16 | - | -9999 | 9999 | 1 | 1 | 50 | 2000 / 5 | 0 | Time Synchronized
Output 1 Activation Time / Turn-on Time | 315 | W/R | Uint_16 | sn | 0 | 240 | 0 | 1 | 51 | 2200 / 5 | 1 | Immediately
Output 1 Deactivation Time / Turn-off Time | 316 | W/R | Uint_16 | sn | 0 | 240 | 0 | 1 | 52 | 2400 / 5
Output 1 Waiting/Hold Time | 317 | W/R | Uint_16 | sn | 0 | 240 | 0 | 1 | 53 | 2500 / 5 | Table-5.2
Pulse Output Energy Magnitude (Table-6.3) | 320 | W/R | Uint_16 | - | 0 | 2 | 0 | 1 | 54 | 2600 / 5 | Index | Unit of Time
Pulse Output Direction (Table-6.4) | 321 | W/R | Uint_16 | - | 0 | 1 | 0 | 1 | 55 | 3000 / 5 | 0 | Minute
Pulse Output Energy Index Value (Table-6.5) | 322 | W/R | Uint_16 | Wh/VArh | 0 | 8 | 0 | 1 | 56 | 3200 / 5 | 1 | Hour
Pulse Output ON Duration | 323 | W/R | Uint_16 | ms | 50 | 1000 | 200 | 1 | 57 | 3500 / 5 | 2 | Day
Pulse Output OFF Duration | 324 | W/R | Uint_16 | ms | 50 | 1000 | 200 | 1 | 58 | 3600 / 5 | 3 | Month
RGP Power Resolution | 330 | W/R | Uint 16 | x100VAr | 1 | 10 | 100 | 1 | 59 | 4000 / 5 | 4 | Indefinite
RGP Maximum Difference | 331 | W/R | Uint 16 | % | 20 | 40 | 40 | 1 | 60 | 4500 / 5
RGP Percentage | 332 | R | Uint 16 | % | 5 | 40 | 5 | 1 | 61 | 5000 / 5 | Table-5.3
Company Name_1 | 340 | W/R | Uint 16 | - | - | - | - | - | 62 | 5500 / 5 | Index | Measurements
Company Name_2 | 341 | W/R | Uint 16 | - | - | - | - | - | 63 | 6000 / 5 | 0 | All Measurements
Company Name_3 | 342 | W/R | Uint 16 | - | - | - | - | - | 64 | 6500 / 5 | 1 | All Harmonics
Company Name_4 | 343 | W/R | Uint 16 | - | - | - | - | - | 65 | 7000 / 5 | 2 | Fundemental Measurements
Company Name_5 | 344 | W/R | Uint 16 | - | - | - | - | - | 66 | 7500 / 5
Company Name_6 | 345 | W/R | Uint 16 | - | - | - | - | - | 67 | 8000 / 5 | Table-5.4
Company Name_7 | 346 | W/R | Uint 16 | - | - | - | - | - | 68 | 8500 / 5 | Index | Formate
Company Name_8 | 347 | W/R | Uint 16 | - | - | - | - | - | 69 | 10000 / 5 | 0 | .csv
Company Name_9 | 348 | W/R | Uint 16 | - | - | - | - | - |  |  | 1 | .GA
Company Name_10 | 349 | W/R | Uint 16 | - | - | - | - | - | Table-2.1
Company Name_11 | 350 | W/R | Uint 16 | - | - | - | - | - | Index | Line Voltage (LN/LL) | Table-6.0
Company Name_12 | 351 | W/R | Uint 16 | - | - | - | - | - | 0 | 50 / 90 V | Index | Output Type
Company Name_13 | 352 | W/R | Uint 16 | - | - | - | - | - | 1 | 60 / 100 V | 0 | Disabled
Company Name_14 | 353 | W/R | Uint 16 | - | - | - | - | - | 2 | 65 / 110 V | 1 | Functional
Company Name_15 | 354 | W/R | Uint 16 | - | - | - | - | - | 3 | 70 / 120 V | 2 | Pulse Output
Company Name_16 | 355 | W/R | Uint 16 | - | - | - | - | - | 4 | 100 / 173 V
Company Name_17 | 356 | W/R | Uint 16 | - | - | - | - | - | 5 | 110 / 190 V | Table-6.1
Company Name_18 | 357 | W/R | Uint 16 | - | - | - | - | - | 6 | 115 / 200 V | Index | Magnitude
Company Name_19 | 358 | W/R | Uint 16 | - | - | - | - | - | 7 | 120 / 208 V | 0 | None
Company Name_20 | 359 | W/R | Uint 16 | - | - | - | - | - | 8 | 130 / 220 V | 1 | Remote Control
Input-1 Edge Trigger Type (Table-7.0) | 370 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 9 | 135 / 230 V | 2 | Voltage
Input-1 Trigger Delay Time | 371 | W/R | Uint 16 | ms | 5 | 10000 | 100 | 1 | 10 | 140 / 240 V | 3 | Current
Input-1 Edge Trigger Enable (Table-7.1) | 372 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 11 | 220 / 380 V | 4 | Frequency
Input-1 Pulse Type (Table-7.2) | 375 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 12 | 230 / 400 V | 5 | Cosine
Input-1 Min. Pulse Width | 376 | W/R | Uint 16 | ms | 5 | 10000 | 200 | 1 | 13 | 240 / 415 V | 6 | Power Factor
Input-1 Tolerance Percentage | 377 | W/R | Uint 16 | % | 3 | 60 | 20 | 1 | 14 | 255 / 440 V | 7 | Tangent
Input-1 Pulse Mode Enable (Table-7.1) | 378 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 15 | 265 / 460 V | 8 | Ratio
Input-2 Edge Trigger Type (Table-7.0) | 385 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 16 | 280 / 480 V | 9 | Active Power
Input-2 Trigger Delay Time | 386 | W/R | Uint 16 | ms | 2 | 10000 | 100 | 1 | 17 | 290 / 500 V | 10 | Reactive Power
Input-2 Edge Trigger Mode (Table-7.1) | 387 | W/R | Uint 16 | - | 0 | 1 | - | - | 18 | 300 / 525 V
Input-2 Pulse Type (Table-7.2) | 390 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 19 | 230 / 550 V | Table-6.2
Input-2 Min. Pulse Width | 391 | W/R | Uint 16 | ms | 5 | 10000 | 200 | 1 | 20 | 345 / 600 V | Index | Phase Selection
Input-2 Tolerance Percentage | 392 | W/R | Uint 16 | % | 3 | 60 | 20 | 1 | 21 | 375 / 650 V | 0 | 3 Phase Average
Input-2 Pulse Mode (Table-7.1) | 393 | W/R | Uint 16 | - | 0 | 1 | 0 | - | 22 | 400 / 690 V | 1 | L1 Phase
Modbus Mode (Table-1.1) | 425 | W/R | Uint 16 | - | 0 | 1 | 0 | 1 | 23 | 420 / 725 V | 2 | L2 Phase
Modbus Data Bits | 426 | R | Uint 16 | - | 7 | 8 | 8 | 1 | 24 | 460 / 800 V | 3 | L3 Phase
Modbus Parity (Table-1.2) | 427 | W/R | Uint 16 | - | 0 | 2 | 0 | 1 | 25 | 490 / 850 V | 4 | Any Phase
Modbus Stop Bits | 428 | W/R | Uint 16 | - | 1 | 2 | 1 | 1 | 26 | 520 / 900 V
Modbus Silence Wait Time | 429 | W/R | Uint 16 | - | 4 | 128 | 8 | 1 | 27 | 575 / 1000 V | Table-6.3
[9 empty] | 28 | 2080 / 3600 V | Index | Energy
[9 empty] | 29 | 3640 / 6300 V | 0 | Active
[9 empty] | 30 | 4160 / 7200 V | 1 | Capacitive
[9 empty] | 31 | 6060 / 10500 V | 2 | Inductive
[9 empty] | 32 | 6350 / 11000 V
[9 empty] | 33 | 6930 / 12000 V | Table-6.4
[9 empty] | 34 | 7970 / 13800 V | Index | Energy
[9 empty] | 35 | 8085 / 14000 V | 0 | In Consumption
[9 empty] | 36 | 8660 / 15000 V | 1 | In Generation
[9 empty] | 37 | 9120 / 15800 V
[9 empty] | 38 | 9815 / 17000 V | Table-6.5
[9 empty] | 39 | 10105 / 17500 V | Index | Energy
[9 empty] | 40 | 13855 / 24000 V | 0 | 1 Wh/VAh
[9 empty] | 41 | 16455 / 28500 V | 1 | 10 Wh/VAh
[9 empty] | 42 | 16680 / 29250 V | 2 | 100 Wh/VAh
[9 empty] | 43 | 17320 / 30000 V | 3 | 1 kWh/kVAh
[9 empty] | 44 | 17755 / 30750 V | 4 | 10 kWh/kVAh
[9 empty] | 45 | 17780 / 30800 V | 5 | 100 kWh/kVAh
[9 empty] | 46 | 18190 / 31500 V | 6 | 1 MWh/MVAh
[9 empty] | 47 | 18475 / 32000 V | 7 | 10 MWh/MVAh
[9 empty] | 48 | 18940 / 32800 V | 8 | 100 MWh/MVAh
[9 empty] | 49 | 19955 / 33000 V
[9 empty] | 50 | 19400 / 33600 V | Table-7.0
[9 empty] | 51 | 19920 / 34500 V | Index | Kenar Tetik Tipi
[9 empty] | 52 | 20210 / 35000 V | 0 | Rising Edge
[9 empty] | 53 | 20440 / 35400 V | 1 | Falling Edge
[9 empty] | 54 | 20785 / 36000 V
[9 empty] | 55 | 20900 / 36200 V | Table-7.1
[9 empty] | 56 | 22230 / 38500 V | Index | Edge Trigger Type
[9 empty] | 57 | 26560 / 46000 V | 0 | Disabled
[11 empty] | 1 | Enabled
Table-7.2
[11 empty] | Index | Pulse Type
[11 empty] | 0 | Positive
[11 empty] | 1 | Negative

## Demands
Demand Values ​​(Consumption) | Adress | Multiplier | Unit | Type | W/R
1. Phase Max Demand Voltage | 12010 | 0.1 | V(Volt) | int32 | R
2. Phase Max Demand Voltage | 12012 | 0.1 | V(Volt) | int32 | R
3. Phase Max Demand Voltage | 12014 | 0.1 | V(Volt) | int32 | R
1. Phase Min Demand Voltage | 12016 | 0.1 | V(Volt) | int32 | R
2. Phase Min Demand Voltage | 12018 | 0.1 | V(Volt) | int32 | R
3. Phase Min Demand Voltage | 12020 | 0.1 | V(Volt) | int32 | R
1. Phase Max Demand Current | 12022 | 0.001 | A(Ampere) | int32 | R
2. Phase Max Demand Current | 12024 | 0.001 | A(Ampere) | int32 | R
3. Phase Max Demand Current | 12026 | 0.001 | A(Ampere) | int32 | R
1. Phase Min Demand Current | 12028 | 0.001 | A(Ampere) | int32 | R
2. Phase Min Demand Current | 12030 | 0.001 | A(Ampere) | int32 | R
3. Phase Min Demand Current | 12032 | 0.001 | A(Ampere) | int32 | R
1. Phase Max Demand Active Power | 12034 | 1 | Watt | int32 | R
2. Phase Max Demand Active Power | 12036 | 1 | Watt | int32 | R
3. Phase Max Demand Active Power | 12038 | 1 | Watt | int32 | R
1. Phase Min Demand Active Power | 12040 | 1 | Watt | int32 | R
2. Phase Min Demand Active Power | 12042 | 1 | Watt | int32 | R
3. Phase Min Demand Active Power | 12044 | 1 | Watt | int32 | R
1. Phase Max Demand Reactive Power | 12046 | 1 | VAR | int32 | R
2. Phase Max Demand Reactive Power | 12048 | 1 | VAR | int32 | R
3. Phase Max Demand Reactive Power | 12050 | 1 | VAR | int32 | R
1. Phase Min Demand Reactive Power | 12052 | 1 | VAR | int32 | R
2. Phase Min Demand Reactive Power | 12054 | 1 | VAR | int32 | R
3. Phase Min Demand Reactive Power | 12056 | 1 | VAR | int32 | R
1. Phase Max Demand Apparent Power | 12058 | 1 | VA | int32 | R
2. Phase Max Demand Apparent Power | 12060 | 1 | VA | int32 | R
3. Phase Max Demand Apparent Power | 12062 | 1 | VA | int32 | R
1. Phase Min Demand Apparent Power | 12064 | 1 | VA | int32 | R
2. Phase Min Demand Apparent Power | 12066 | 1 | VA | int32 | R
3. Phase Min Demand Apparent Power | 12068 | 1 | VA | int32 | R
1. Phase Max Demand THVD | 12100 | 0.1 | % | int32 | R
2. Phase Max Demand THVD | 12102 | 0.1 | % | int32 | R
3. Phase Max Demand THVD | 12104 | 0.1 | % | int32 | R
1. Phase Min Demand THVD | 12106 | 0.1 | % | int32 | R
2. Phase Min Demand THVD | 12108 | 0.1 | % | int32 | R
3. Phase Min Demand THVD | 12110 | 0.1 | % | int32 | R
1. Phase Max Demand THID | 12112 | 0.1 | % | int32 | R
2. Phase Max Demand THID | 12114 | 0.1 | % | int32 | R
3. Phase Max Demand THID | 12116 | 0.1 | % | int32 | R
1. Phase Min Demand THID | 12118 | 0.1 | % | int32 | R
2. Phase Min Demand THID | 12120 | 0.1 | % | int32 | R
3. Phase Min Demand THID | 12122 | 0.1 | % | int32 | R
Demand Values (Export/Generation) | Adress | Multiplier | Unit | Type | W/R
1. Phase Max Demand Voltage | 12260 | 0.1 | V(Volt) | int32 | R
2. Phase Max Demand Voltage | 12262 | 0.1 | V(Volt) | int32 | R
3. Phase Max Demand Voltage | 12264 | 0.1 | V(Volt) | int32 | R
1. Phase Min Demand Voltage | 12266 | 0.1 | V(Volt) | int32 | R
2. Phase Min Demand Voltage | 12268 | 0.1 | V(Volt) | int32 | R
3. Phase Min Demand Voltage | 12270 | 0.1 | V(Volt) | int32 | R
1. Phase Max Demand Current | 12272 | 1 | A(Ampere) | int32 | R
2. Phase Max Demand Current | 12274 | 1 | A(Ampere) | int32 | R
3. Phase Max Demand Current | 12276 | 1 | A(Ampere) | int32 | R
1. Phase Min Demand Current | 12278 | 1 | A(Ampere) | int32 | R
2. Phase Min Demand Current | 12280 | 1 | A(Ampere) | int32 | R
3. Phase Min Demand Current | 12282 | 1 | A(Ampere) | int32 | R
1. Phase Max Demand Active Power | 12284 | 1 | Watt | int32 | R
2. Phase Max Demand Active Power | 12286 | 1 | Watt | int32 | R
3. Phase Max Demand Active Power | 12288 | 1 | Watt | int32 | R
1. Phase Min Demand Active Power | 12290 | 1 | Watt | int32 | R
2. Phase Min Demand Active Power | 12292 | 1 | Watt | int32 | R
3. Phase Min Demand Active Power | 12294 | 1 | Watt | int32 | R
1. Phase Max Demand Reactive Power | 12296 | 1 | VAR | int32 | R
2. Phase Max Demand Reactive Power | 12298 | 1 | VAR | int32 | R
3. Phase Max Demand Reactive Power | 12300 | 1 | VAR | int32 | R
1. Phase Min Demand Reactive Power | 12302 | 1 | VAR | int32 | R
2. Phase Min Demand Reactive Power | 12304 | 1 | VAR | int32 | R
3. Phase Min Demand Reactive Power | 12306 | 1 | VAR | int32 | R
1. Phase Max Demand Apparent Power | 12308 | 1 | VA | int32 | R
2. Phase Max Demand Apparent Power | 12310 | 1 | VA | int32 | R
3. Phase Max Demand Apparent Power | 12312 | 1 | VA | int32 | R
1. Phase Min Demand Apparent Power | 12314 | 1 | VA | int32 | R
2. Phase Min Demand Apparent Power | 12316 | 1 | VA | int32 | R
3. Phase Min Demand Apparent Power | 12318 | 1 | VA | int32 | R
1. Phase Max Demand THVD | 12350 | 0.1 | % | int32 | R
2. Phase Max Demand THVD | 12352 | 0.1 | % | int32 | R
3. Phase Max Demand THVD | 12354 | 0.1 | % | int32 | R
1. Phase Min Demand THVD | 12356 | 0.1 | % | int32 | R
2. Phase Min Demand THVD | 12358 | 0.1 | % | int32 | R
3. Phase Min Demand THVD | 12360 | 0.1 | % | int32 | R
1. Phase Max Demand THID | 12362 | 0.1 | % | int32 | R
2. Phase Max Demand THID | 12364 | 0.1 | % | int32 | R
3. Phase Max Demand THID | 12366 | 0.1 | % | int32 | R
1. Phase Min Demand THID | 12368 | 0.1 | % | int32 | R
2. Phase Min Demand THID | 12370 | 0.1 | % | int32 | R
3. Phase Min Demand THID | 12372 | 0.1 | % | int32 | R

## Energies
Energy Values (Consumption/Import) | Adress | Multiplier | Unit | Type | W/R
Total Active Energy | 13020 | 1 | Wh | uint64 | R
Total Inductive Energy | 13024 | 1 | VARh | uint64 | R
Total Capacitive Energy | 13028 | 1 | VARh | uint64 | R
1. Phase Active Energy | 13032 | 1 | Wh | uint64 | R
2. Phase Active Energy | 13036 | 1 | Wh | uint64 | R
3. Phase Active Energy | 13040 | 1 | Wh | uint64 | R
1. Phase Inductive Energy | 13044 | 1 | VARh | uint64 | R
2. Phase Inductive Energy | 13048 | 1 | VARh | uint64 | R
3. Phase Inductive Energy | 13052 | 1 | VARh | uint64 | R
1. Phase Capacitive Energy | 13056 | 1 | VARh | uint64 | R
2. Phase Capacitive Energy | 13060 | 1 | VARh | uint64 | R
3. Phase Capacitive Energy | 13064 | 1 | VARh | uint64 | R
Input-1 Edge Trigger Unit Energy | 10100 | 1 | Wh | uint64 | R
Input-1 Pulse Unit Energy | 10104 | 1 | Wh | uint64 | R
Input-2 Edge Trigger Unit Energy | 10108 | 1 | Wh | uint64 | R
Input-2 Pulse Unit Energy | 10112 | 1 | Wh | uint64 | R
Energy Values (Generation/Export) | Adress | Multiplier | Unit | Type | W/R
Total Active Energy | 13280 | 1 | Wh | uint64 | R
Total Inductive Energy | 13284 | 1 | VARh | uint64 | R
Total Capacitive Energy | 13288 | 1 | VARh | uint64 | R
1. Phase Active Energy | 13292 | 1 | Wh | uint64 | R
2. Phase Active Energy | 13296 | 1 | Wh | uint64 | R
3. Phase Active Energy | 13300 | 1 | Wh | uint64 | R
1. Phase Inductive Energy | 13304 | 1 | VARh | uint64 | R
2. Phase Inductive Energy | 13308 | 1 | VARh | uint64 | R
3. Phase Inductive Energy | 13312 | 1 | VARh | uint64 | R
1. Phase Capacitive Energy | 13316 | 1 | VARh | uint64 | R
2. Phase Capacitive Energy | 13320 | 1 | VARh | uint64 | R
3. Phase Capacitive Energy | 13324 | 1 | VARh | uint64 | R

## Voltage Harmonics
Voltage Harmonic Distortion (Odd) | Adress | Multiplier | Index | Type | W/R | Voltage Harmonic Distortion (Even) | Adress | Multiplier | Index | Type | W/R
Odd/Even Profile | 19998 | - |  | int16 | R | Odd/Even Profile | 20098 | - |  | int16 | R
Harmonic Limit | 19999 | - |  | int16 | R | Harmonic Limit | 20099 | - |  | int16 | R
1. Phase THVD | 20000 | 0.1 | % | int16 | R | 1. Phase THVD | 20100 | 0.1 | % | int16 | R
2. Phase THVD | 20001 | 0.1 | % | int16 | R | 2. Phase THVD | 20101 | 0.1 | % | int16 | R
3. Phase THVD | 20002 | 0.1 | % | int16 | R | 3. Phase THVD | 20102 | 0.1 | % | int16 | R
3rd Harmonic L1 | 20003 | 0.1 | % | int16 | R | 2nd Harmonic L1 | 20103 | 0.1 | % | int16 | R
3rd Harmonic L2 | 20004 | 0.1 | % | int16 | R | 2nd Harmonic L2 | 20104 | 0.1 | % | int16 | R
3rd Harmonic L3 | 20005 | 0.1 | % | int16 | R | 2nd Harmonic L3 | 20105 | 0.1 | % | int16 | R
5th Harmonic L1 | 20006 | 0.1 | % | int16 | R | 4th Harmonic L1 | 20106 | 0.1 | % | int16 | R
5th Harmonic L2 | 20007 | 0.1 | % | int16 | R | 4th Harmonic L2 | 20107 | 0.1 | % | int16 | R
5th Harmonic L3 | 20008 | 0.1 | % | int16 | R | 4th Harmonic L3 | 20108 | 0.1 | % | int16 | R
7th Harmonic L1 | 20009 | 0.1 | % | int16 | R | 6th Harmonic L1 | 20109 | 0.1 | % | int16 | R
7th Harmonic L2 | 20010 | 0.1 | % | int16 | R | 6th Harmonic L2 | 20110 | 0.1 | % | int16 | R
7th Harmonic L3 | 20011 | 0.1 | % | int16 | R | 6th Harmonic L3 | 20111 | 0.1 | % | int16 | R
9th Harmonic L1 | 20012 | 0.1 | % | int16 | R | 8th Harmonic L1 | 20112 | 0.1 | % | int16 | R
9th Harmonic L2 | 20013 | 0.1 | % | int16 | R | 8th Harmonic L2 | 20113 | 0.1 | % | int16 | R
9th Harmonic L3 | 20014 | 0.1 | % | int16 | R | 8th Harmonic L3 | 20114 | 0.1 | % | int16 | R
11th Harmonic L1 | 20015 | 0.1 | % | int16 | R | 10th Harmonic L1 | 20115 | 0.1 | % | int16 | R
11th Harmonic L2 | 20016 | 0.1 | % | int16 | R | 10th Harmonic L2 | 20116 | 0.1 | % | int16 | R
11th Harmonic L3 | 20017 | 0.1 | % | int16 | R | 10th Harmonic L3 | 20117 | 0.1 | % | int16 | R
13th Harmonic L1 | 20018 | 0.1 | % | int16 | R | 12th Harmonic L1 | 20118 | 0.1 | % | int16 | R
13th Harmonic L2 | 20019 | 0.1 | % | int16 | R | 12th Harmonic L2 | 20119 | 0.1 | % | int16 | R
13th Harmonic L3 | 20020 | 0.1 | % | int16 | R | 12th Harmonic L3 | 20120 | 0.1 | % | int16 | R
15th Harmonic L1 | 20021 | 0.1 | % | int16 | R | 14th Harmonic L1 | 20121 | 0.1 | % | int16 | R
15th Harmonic L2 | 20022 | 0.1 | % | int16 | R | 14th Harmonic L2 | 20122 | 0.1 | % | int16 | R
15th Harmonic L3 | 20023 | 0.1 | % | int16 | R | 14th Harmonic L3 | 20123 | 0.1 | % | int16 | R
17th Harmonic L1 | 20024 | 0.1 | % | int16 | R | 16th Harmonic L1 | 20124 | 0.1 | % | int16 | R
17th Harmonic L2 | 20025 | 0.1 | % | int16 | R | 16th Harmonic L2 | 20125 | 0.1 | % | int16 | R
17th Harmonic L3 | 20026 | 0.1 | % | int16 | R | 16th Harmonic L3 | 20126 | 0.1 | % | int16 | R
19th Harmonic L1 | 20027 | 0.1 | % | int16 | R | 18th Harmonic L1 | 20127 | 0.1 | % | int16 | R
19th Harmonic L2 | 20028 | 0.1 | % | int16 | R | 18th Harmonic L2 | 20128 | 0.1 | % | int16 | R
19th Harmonic L3 | 20029 | 0.1 | % | int16 | R | 18th Harmonic L3 | 20129 | 0.1 | % | int16 | R
21st Harmonic L1 | 20030 | 0.1 | % | int16 | R | 20th Harmonic L1 | 20130 | 0.1 | % | int16 | R
21st Harmonic L2 | 20031 | 0.1 | % | int16 | R | 20th Harmonic L2 | 20131 | 0.1 | % | int16 | R
21st Harmonic L3 | 20032 | 0.1 | % | int16 | R | 20th Harmonic L3 | 20132 | 0.1 | % | int16 | R
23rd Harmonic L1 | 20033 | 0.1 | % | int16 | R | 22nd Harmonic L1 | 20133 | 0.1 | % | int16 | R
23rd Harmonic L2 | 20034 | 0.1 | % | int16 | R | 22nd Harmonic L2 | 20134 | 0.1 | % | int16 | R
23rd Harmonic L3 | 20035 | 0.1 | % | int16 | R | 22nd Harmonic L3 | 20135 | 0.1 | % | int16 | R
25th Harmonic L1 | 20036 | 0.1 | % | int16 | R | 24th Harmonic L1 | 20136 | 0.1 | % | int16 | R
25th Harmonic L2 | 20037 | 0.1 | % | int16 | R | 24th Harmonic L2 | 20137 | 0.1 | % | int16 | R
25th Harmonic L3 | 20038 | 0.1 | % | int16 | R | 24th Harmonic L3 | 20138 | 0.1 | % | int16 | R
27th Harmonic L1 | 20039 | 0.1 | % | int16 | R | 26th Harmonic L1 | 20139 | 0.1 | % | int16 | R
27th Harmonic L2 | 20040 | 0.1 | % | int16 | R | 26th Harmonic L2 | 20140 | 0.1 | % | int16 | R
27th Harmonic L3 | 20041 | 0.1 | % | int16 | R | 26th Harmonic L3 | 20141 | 0.1 | % | int16 | R
29th Harmonic L1 | 20042 | 0.1 | % | int16 | R | 28th Harmonic L1 | 20142 | 0.1 | % | int16 | R
29th Harmonic L2 | 20043 | 0.1 | % | int16 | R | 28th Harmonic L2 | 20143 | 0.1 | % | int16 | R
29th Harmonic L3 | 20044 | 0.1 | % | int16 | R | 28th Harmonic L3 | 20144 | 0.1 | % | int16 | R
31st Harmonic L1 | 20045 | 0.1 | % | int16 | R | 30th Harmonic L1 | 20145 | 0.1 | % | int16 | R
31st Harmonic L2 | 20046 | 0.1 | % | int16 | R | 30th Harmonic L2 | 20146 | 0.1 | % | int16 | R
31st Harmonic L3 | 20047 | 0.1 | % | int16 | R | 30th Harmonic L3 | 20147 | 0.1 | % | int16 | R
33rd Harmonic L1 | 20048 | 0.1 | % | int16 | R | 32nd Harmonic L1 | 20148 | 0.1 | % | int16 | R
33rd Harmonic L2 | 20049 | 0.1 | % | int16 | R | 32nd Harmonic L2 | 20149 | 0.1 | % | int16 | R
33rd Harmonic L3 | 20050 | 0.1 | % | int16 | R | 32nd Harmonic L3 | 20150 | 0.1 | % | int16 | R
35th Harmonic L1 | 20051 | 0.1 | % | int16 | R | 34th Harmonic L1 | 20151 | 0.1 | % | int16 | R
35th Harmonic L2 | 20052 | 0.1 | % | int16 | R | 34th Harmonic L2 | 20152 | 0.1 | % | int16 | R
35th Harmonic L3 | 20053 | 0.1 | % | int16 | R | 34th Harmonic L3 | 20153 | 0.1 | % | int16 | R
37th Harmonic L1 | 20054 | 0.1 | % | int16 | R | 36th Harmonic L1 | 20154 | 0.1 | % | int16 | R
37th Harmonic L2 | 20055 | 0.1 | % | int16 | R | 36th Harmonic L2 | 20155 | 0.1 | % | int16 | R
37th Harmonic L3 | 20056 | 0.1 | % | int16 | R | 36th Harmonic L3 | 20156 | 0.1 | % | int16 | R
39th Harmonic L1 | 20057 | 0.1 | % | int16 | R | 38th Harmonic L1 | 20157 | 0.1 | % | int16 | R
39th Harmonic L2 | 20058 | 0.1 | % | int16 | R | 38th Harmonic L2 | 20158 | 0.1 | % | int16 | R
39th Harmonic L3 | 20059 | 0.1 | % | int16 | R | 38th Harmonic L3 | 20159 | 0.1 | % | int16 | R
41st Harmonic L1 | 20060 | 0.1 | % | int16 | R | 40th Harmonic L1 | 20160 | 0.1 | % | int16 | R
41st Harmonic L2 | 20061 | 0.1 | % | int16 | R | 40th Harmonic L2 | 20161 | 0.1 | % | int16 | R
41st Harmonic L3 | 20062 | 0.1 | % | int16 | R | 40th Harmonic L3 | 20162 | 0.1 | % | int16 | R
43rd Harmonic L1 | 20063 | 0.1 | % | int16 | R | 42nd Harmonic L1 | 20163 | 0.1 | % | int16 | R
43rd Harmonic L2 | 20064 | 0.1 | % | int16 | R | 42nd Harmonic L2 | 20164 | 0.1 | % | int16 | R
43rd Harmonic L3 | 20065 | 0.1 | % | int16 | R | 42nd Harmonic L3 | 20165 | 0.1 | % | int16 | R
45th Harmonic L1 | 20066 | 0.1 | % | int16 | R | 44th Harmonic L1 | 20166 | 0.1 | % | int16 | R
45th Harmonic L2 | 20067 | 0.1 | % | int16 | R | 44th Harmonic L2 | 20167 | 0.1 | % | int16 | R
45th Harmonic L3 | 20068 | 0.1 | % | int16 | R | 44th Harmonic L3 | 20168 | 0.1 | % | int16 | R
47th Harmonic L1 | 20069 | 0.1 | % | int16 | R | 46th Harmonic L1 | 20169 | 0.1 | % | int16 | R
47th Harmonic L2 | 20070 | 0.1 | % | int16 | R | 46th Harmonic L2 | 20170 | 0.1 | % | int16 | R
47th Harmonic L3 | 20071 | 0.1 | % | int16 | R | 46th Harmonic L3 | 20171 | 0.1 | % | int16 | R
49th Harmonic L1 | 20072 | 0.1 | % | int16 | R | 48th Harmonic L1 | 20172 | 0.1 | % | int16 | R
49th Harmonic L2 | 20073 | 0.1 | % | int16 | R | 48th Harmonic L2 | 20173 | 0.1 | % | int16 | R
49th Harmonic L3 | 20074 | 0.1 | % | int16 | R | 48th Harmonic L3 | 20174 | 0.1 | % | int16 | R
51st Harmonic L1 | 20075 | 0.1 | % | int16 | R | 50th Harmonic L1 | 20175 | 0.1 | % | int16 | R
51st Harmonic L2 | 20076 | 0.1 | % | int16 | R | 50th Harmonic L2 | 20176 | 0.1 | % | int16 | R
51st Harmonic L3 | 20077 | 0.1 | % | int16 | R | 50th Harmonic L3 | 20177 | 0.1 | % | int16 | R
53rd Harmonic L1 | 20078 | 0.1 | % | int16 | R | 52nd Harmonic L1 | 20178 | 0.1 | % | int16 | R
53rd Harmonic L2 | 20079 | 0.1 | % | int16 | R | 52nd Harmonic L2 | 20179 | 0.1 | % | int16 | R
53rd Harmonic L3 | 20080 | 0.1 | % | int16 | R | 52nd Harmonic L3 | 20180 | 0.1 | % | int16 | R
55th Harmonic L1 | 20081 | 0.1 | % | int16 | R | 54th Harmonic L1 | 20181 | 0.1 | % | int16 | R
55th Harmonic L2 | 20082 | 0.1 | % | int16 | R | 54th Harmonic L2 | 20182 | 0.1 | % | int16 | R
55th Harmonic L3 | 20083 | 0.1 | % | int16 | R | 54th Harmonic L3 | 20183 | 0.1 | % | int16 | R
57th Harmonic L1 | 20084 | 0.1 | % | int16 | R | 56th Harmonic L1 | 20184 | 0.1 | % | int16 | R
57th Harmonic L2 | 20085 | 0.1 | % | int16 | R | 56th Harmonic L2 | 20185 | 0.1 | % | int16 | R
57th Harmonic L3 | 20086 | 0.1 | % | int16 | R | 56th Harmonic L3 | 20186 | 0.1 | % | int16 | R
59th Harmonic L1 | 20087 | 0.1 | % | int16 | R | 58th Harmonic L1 | 20187 | 0.1 | % | int16 | R
59th Harmonic L2 | 20088 | 0.1 | % | int16 | R | 58th Harmonic L2 | 20188 | 0.1 | % | int16 | R
59th Harmonic L3 | 20089 | 0.1 | % | int16 | R | 58th Harmonic L3 | 20189 | 0.1 | % | int16 | R
61st Harmonic L1 | 20090 | 0.1 | % | int16 | R | 60th Harmonic L1 | 20190 | 0.1 | % | int16 | R
61st Harmonic L2 | 20091 | 0.1 | % | int16 | R | 60th Harmonic L2 | 20191 | 0.1 | % | int16 | R
61st Harmonic L3 | 20092 | 0.1 | % | int16 | R | 60th Harmonic L3 | 20192 | 0.1 | % | int16 | R
63rd Harmonic L1 | 20093 | 0.1 | % | int16 | R | 62nd Harmonic L1 | 20193 | 0.1 | % | int16 | R
63rd Harmonic L2 | 20094 | 0.1 | % | int16 | R | 62nd Harmonic L2 | 20194 | 0.1 | % | int16 | R
63rd Harmonic L3 | 20095 | 0.1 | % | int16 | R | 62nd Harmonic L3 | 20195 | 0.1 | % | int16 | R
Voltage Harmonic RMS (Odd) | Adress | Multiplier | Index | Type | W/R | Voltage Harmonic RMS (Even) | Adress | Multiplier | Index | Type | W/R
Odd/Even Profile | 20246 | - |  | int16 | R | Odd/Even Profile | 20446 | - |  | int16 | R
Harmonic Limit | 20248 | - |  | int16 | R | Harmonic Limit | 20448 | - |  | int16 | R
1. Phase Fundamental Component | 20250 | 0.1 |  | int32 | R | 1. Phase Fundamental Component | 20500 | 0.1 |  | int32 | R
2. Phase Fundamental Component | 20252 | 0.1 |  | int32 | R | 2. Phase Fundamental Component | 20502 | 0.1 |  | int32 | R
3. Phase Fundamental Component | 20254 | 0.1 |  | int32 | R | 3. Phase Fundamental Component | 20504 | 0.1 |  | int32 | R
3rd Harmonic L1 | 20256 | 0.1 |  | int32 | R | 2nd Harmonic L1 | 20506 | 0.1 |  | int32 | R
3rd Harmonic L2 | 20258 | 0.1 |  | int32 | R | 2nd Harmonic L2 | 20508 | 0.1 |  | int32 | R
3rd Harmonic L3 | 20260 | 0.1 |  | int32 | R | 2nd Harmonic L3 | 20510 | 0.1 |  | int32 | R
5th Harmonic L1 | 20262 | 0.1 |  | int32 | R | 4th Harmonic L1 | 20512 | 0.1 |  | int32 | R
5th Harmonic L2 | 20264 | 0.1 |  | int32 | R | 4th Harmonic L2 | 20514 | 0.1 |  | int32 | R
5th Harmonic L3 | 20266 | 0.1 |  | int32 | R | 4th Harmonic L3 | 20516 | 0.1 |  | int32 | R
7th Harmonic L1 | 20268 | 0.1 |  | int32 | R | 6th Harmonic L1 | 20518 | 0.1 |  | int32 | R
7th Harmonic L2 | 20270 | 0.1 |  | int32 | R | 6th Harmonic L2 | 20520 | 0.1 |  | int32 | R
7th Harmonic L3 | 20272 | 0.1 |  | int32 | R | 6th Harmonic L3 | 20522 | 0.1 |  | int32 | R
9th Harmonic L1 | 20274 | 0.1 |  | int32 | R | 8th Harmonic L1 | 20524 | 0.1 |  | int32 | R
9th Harmonic L2 | 20276 | 0.1 |  | int32 | R | 8th Harmonic L2 | 20526 | 0.1 |  | int32 | R
9th Harmonic L3 | 20278 | 0.1 |  | int32 | R | 8th Harmonic L3 | 20528 | 0.1 |  | int32 | R
11th Harmonic L1 | 20280 | 0.1 |  | int32 | R | 10th Harmonic L1 | 20530 | 0.1 |  | int32 | R
11th Harmonic L2 | 20282 | 0.1 |  | int32 | R | 10th Harmonic L2 | 20532 | 0.1 |  | int32 | R
11th Harmonic L3 | 20284 | 0.1 |  | int32 | R | 10th Harmonic L3 | 20534 | 0.1 |  | int32 | R
13th Harmonic L1 | 20286 | 0.1 |  | int32 | R | 12th Harmonic L1 | 20536 | 0.1 |  | int32 | R
13th Harmonic L2 | 20288 | 0.1 |  | int32 | R | 12th Harmonic L2 | 20538 | 0.1 |  | int32 | R
13th Harmonic L3 | 20290 | 0.1 |  | int32 | R | 12th Harmonic L3 | 20540 | 0.1 |  | int32 | R
15th Harmonic L1 | 20292 | 0.1 |  | int32 | R | 14th Harmonic L1 | 20542 | 0.1 |  | int32 | R
15th Harmonic L2 | 20294 | 0.1 |  | int32 | R | 14th Harmonic L2 | 20544 | 0.1 |  | int32 | R
15th Harmonic L3 | 20296 | 0.1 |  | int32 | R | 14th Harmonic L3 | 20546 | 0.1 |  | int32 | R
17th Harmonic L1 | 20298 | 0.1 |  | int32 | R | 16th Harmonic L1 | 20548 | 0.1 |  | int32 | R
17th Harmonic L2 | 20300 | 0.1 |  | int32 | R | 16th Harmonic L2 | 20550 | 0.1 |  | int32 | R
17th Harmonic L3 | 20302 | 0.1 |  | int32 | R | 16th Harmonic L3 | 20552 | 0.1 |  | int32 | R
19th Harmonic L1 | 20304 | 0.1 |  | int32 | R | 18th Harmonic L1 | 20554 | 0.1 |  | int32 | R
19th Harmonic L2 | 20306 | 0.1 |  | int32 | R | 18th Harmonic L2 | 20556 | 0.1 |  | int32 | R
19th Harmonic L3 | 20308 | 0.1 |  | int32 | R | 18th Harmonic L3 | 20558 | 0.1 |  | int32 | R
21st Harmonic L1 | 20310 | 0.1 |  | int32 | R | 20th Harmonic L1 | 20560 | 0.1 |  | int32 | R
21st Harmonic L2 | 20312 | 0.1 |  | int32 | R | 20th Harmonic L2 | 20562 | 0.1 |  | int32 | R
21st Harmonic L3 | 20314 | 0.1 |  | int32 | R | 20th Harmonic L3 | 20564 | 0.1 |  | int32 | R
23rd Harmonic L1 | 20316 | 0.1 |  | int32 | R | 22nd Harmonic L1 | 20566 | 0.1 |  | int32 | R
23rd Harmonic L2 | 20318 | 0.1 |  | int32 | R | 22nd Harmonic L2 | 20568 | 0.1 |  | int32 | R
23rd Harmonic L3 | 20320 | 0.1 |  | int32 | R | 22nd Harmonic L3 | 20570 | 0.1 |  | int32 | R
25th Harmonic L1 | 20322 | 0.1 |  | int32 | R | 24th Harmonic L1 | 20572 | 0.1 |  | int32 | R
25th Harmonic L2 | 20324 | 0.1 |  | int32 | R | 24th Harmonic L2 | 20574 | 0.1 |  | int32 | R
25th Harmonic L3 | 20326 | 0.1 |  | int32 | R | 24th Harmonic L3 | 20576 | 0.1 |  | int32 | R
27th Harmonic L1 | 20328 | 0.1 |  | int32 | R | 26th Harmonic L1 | 20578 | 0.1 |  | int32 | R
27th Harmonic L2 | 20330 | 0.1 |  | int32 | R | 26th Harmonic L2 | 20580 | 0.1 |  | int32 | R
27th Harmonic L3 | 20332 | 0.1 |  | int32 | R | 26th Harmonic L3 | 20582 | 0.1 |  | int32 | R
29th Harmonic L1 | 20334 | 0.1 |  | int32 | R | 28th Harmonic L1 | 20584 | 0.1 |  | int32 | R
29th Harmonic L2 | 20336 | 0.1 |  | int32 | R | 28th Harmonic L2 | 20586 | 0.1 |  | int32 | R
29th Harmonic L3 | 20338 | 0.1 |  | int32 | R | 28th Harmonic L3 | 20588 | 0.1 |  | int32 | R
31st Harmonic L1 | 20340 | 0.1 |  | int32 | R | 30th Harmonic L1 | 20590 | 0.1 |  | int32 | R
31st Harmonic L2 | 20342 | 0.1 |  | int32 | R | 30th Harmonic L2 | 20592 | 0.1 |  | int32 | R
31st Harmonic L3 | 20344 | 0.1 |  | int32 | R | 30th Harmonic L3 | 20594 | 0.1 |  | int32 | R
33rd Harmonic L1 | 20346 | 0.1 |  | int32 | R | 32nd Harmonic L1 | 20596 | 0.1 |  | int32 | R
33rd Harmonic L2 | 20348 | 0.1 |  | int32 | R | 32nd Harmonic L2 | 20598 | 0.1 |  | int32 | R
33rd Harmonic L3 | 20350 | 0.1 |  | int32 | R | 32nd Harmonic L3 | 20600 | 0.1 |  | int32 | R
35th Harmonic L1 | 20352 | 0.1 |  | int32 | R | 34th Harmonic L1 | 20602 | 0.1 |  | int32 | R
35th Harmonic L2 | 20354 | 0.1 |  | int32 | R | 34th Harmonic L2 | 20604 | 0.1 |  | int32 | R
35th Harmonic L3 | 20356 | 0.1 |  | int32 | R | 34th Harmonic L3 | 20606 | 0.1 |  | int32 | R
37th Harmonic L1 | 20358 | 0.1 |  | int32 | R | 36th Harmonic L1 | 20608 | 0.1 |  | int32 | R
37th Harmonic L2 | 20360 | 0.1 |  | int32 | R | 36th Harmonic L2 | 20610 | 0.1 |  | int32 | R
37th Harmonic L3 | 20362 | 0.1 |  | int32 | R | 36th Harmonic L3 | 20612 | 0.1 |  | int32 | R
39th Harmonic L1 | 20364 | 0.1 |  | int32 | R | 38th Harmonic L1 | 20614 | 0.1 |  | int32 | R
39th Harmonic L2 | 20366 | 0.1 |  | int32 | R | 38th Harmonic L2 | 20616 | 0.1 |  | int32 | R
39th Harmonic L3 | 20368 | 0.1 |  | int32 | R | 38th Harmonic L3 | 20618 | 0.1 |  | int32 | R
41st Harmonic L1 | 20370 | 0.1 |  | int32 | R | 40th Harmonic L1 | 20620 | 0.1 |  | int32 | R
41st Harmonic L2 | 20372 | 0.1 |  | int32 | R | 40th Harmonic L2 | 20622 | 0.1 |  | int32 | R
41st Harmonic L3 | 20374 | 0.1 |  | int32 | R | 40th Harmonic L3 | 20624 | 0.1 |  | int32 | R
43rd Harmonic L1 | 20376 | 0.1 |  | int32 | R | 42nd Harmonic L1 | 20626 | 0.1 |  | int32 | R
43rd Harmonic L2 | 20378 | 0.1 |  | int32 | R | 42nd Harmonic L2 | 20628 | 0.1 |  | int32 | R
43rd Harmonic L3 | 20380 | 0.1 |  | int32 | R | 42nd Harmonic L3 | 20630 | 0.1 |  | int32 | R
45th Harmonic L1 | 20382 | 0.1 |  | int32 | R | 44th Harmonic L1 | 20632 | 0.1 |  | int32 | R
45th Harmonic L2 | 20384 | 0.1 |  | int32 | R | 44th Harmonic L2 | 20634 | 0.1 |  | int32 | R
45th Harmonic L3 | 20386 | 0.1 |  | int32 | R | 44th Harmonic L3 | 20636 | 0.1 |  | int32 | R
47th Harmonic L1 | 20388 | 0.1 |  | int32 | R | 46th Harmonic L1 | 20638 | 0.1 |  | int32 | R
47th Harmonic L2 | 20390 | 0.1 |  | int32 | R | 46th Harmonic L2 | 20640 | 0.1 |  | int32 | R
47th Harmonic L3 | 20392 | 0.1 |  | int32 | R | 46th Harmonic L3 | 20642 | 0.1 |  | int32 | R
49th Harmonic L1 | 20394 | 0.1 |  | int32 | R | 48th Harmonic L1 | 20644 | 0.1 |  | int32 | R
49th Harmonic L2 | 20396 | 0.1 |  | int32 | R | 48th Harmonic L2 | 20646 | 0.1 |  | int32 | R
49th Harmonic L3 | 20398 | 0.1 |  | int32 | R | 48th Harmonic L3 | 20648 | 0.1 |  | int32 | R
51st Harmonic L1 | 20400 | 0.1 |  | int32 | R | 50th Harmonic L1 | 20650 | 0.1 |  | int32 | R
51st Harmonic L2 | 20402 | 0.1 |  | int32 | R | 50th Harmonic L2 | 20652 | 0.1 |  | int32 | R
51st Harmonic L3 | 20404 | 0.1 |  | int32 | R | 50th Harmonic L3 | 20654 | 0.1 |  | int32 | R
53rd Harmonic L1 | 20406 | 0.1 |  | int32 | R | 52nd Harmonic L1 | 20656 | 0.1 |  | int32 | R
53rd Harmonic L2 | 20408 | 0.1 |  | int32 | R | 52nd Harmonic L2 | 20658 | 0.1 |  | int32 | R
53rd Harmonic L3 | 20410 | 0.1 |  | int32 | R | 52nd Harmonic L3 | 20660 | 0.1 |  | int32 | R
55th Harmonic L1 | 20412 | 0.1 |  | int32 | R | 54th Harmonic L1 | 20662 | 0.1 |  | int32 | R
55th Harmonic L2 | 20414 | 0.1 |  | int32 | R | 54th Harmonic L2 | 20664 | 0.1 |  | int32 | R
55th Harmonic L3 | 20416 | 0.1 |  | int32 | R | 54th Harmonic L3 | 20666 | 0.1 |  | int32 | R
57th Harmonic L1 | 20418 | 0.1 |  | int32 | R | 56th Harmonic L1 | 20668 | 0.1 |  | int32 | R
57th Harmonic L2 | 20420 | 0.1 |  | int32 | R | 56th Harmonic L2 | 20670 | 0.1 |  | int32 | R
57th Harmonic L3 | 20422 | 0.1 |  | int32 | R | 56th Harmonic L3 | 20672 | 0.1 |  | int32 | R
59th Harmonic L1 | 20424 | 0.1 |  | int32 | R | 58th Harmonic L1 | 20674 | 0.1 |  | int32 | R
59th Harmonic L2 | 20426 | 0.1 |  | int32 | R | 58th Harmonic L2 | 20676 | 0.1 |  | int32 | R
59th Harmonic L3 | 20428 | 0.1 |  | int32 | R | 58th Harmonic L3 | 20678 | 0.1 |  | int32 | R
61st Harmonic L1 | 20430 | 0.1 |  | int32 | R | 60th Harmonic L1 | 20680 | 0.1 |  | int32 | R
61st Harmonic L2 | 20432 | 0.1 |  | int32 | R | 60th Harmonic L2 | 20682 | 0.1 |  | int32 | R
61st Harmonic L3 | 20434 | 0.1 |  | int32 | R | 60th Harmonic L3 | 20684 | 0.1 |  | int32 | R
63rd Harmonic L1 | 20436 | 0.1 |  | int32 | R | 62nd Harmonic L1 | 20686 | 0.1 |  | int32 | R
63rd Harmonic L2 | 20438 | 0.1 |  | int32 | R | 62nd Harmonic L2 | 20688 | 0.1 |  | int32 | R
63rd Harmonic L3 | 20440 | 0.1 |  | int32 | R | 62nd Harmonic L3 | 20690 | 0.1 |  | int32 | R

## Current Harmonics
Current Harmonic Distortion (Odd) | Adress | Multiplier | Index | Type | W/R | Current Harmonic Distortion (Even) | Adress | Multiplier | Index | Type | W/R
Odd/Even Profile | 29998 | - |  | int16 | R | Odd/Even Profile | 30098 | - |  | int16 | R
Harmonic Limit | 29999 | - |  | int16 | R | Harmonic Limit | 30099 | - |  | int16 | R
1. Phase THID | 30000 | 0.1 | % | int16 | R | 1. Phase THID | 30100 | 0.1 | % | int16 | R
2. Phase THID | 30001 | 0.1 | % | int16 | R | 2. Phase THID | 30101 | 0.1 | % | int16 | R
3. Phase THID | 30002 | 0.1 | % | int16 | R | 3. Phase THID | 30102 | 0.1 | % | int16 | R
3rd Harmonic L1 | 30003 | 0.1 | % | int16 | R | 2nd Harmonic L1 | 30103 | 0.1 | % | int16 | R
3rd Harmonic L2 | 30004 | 0.1 | % | int16 | R | 2nd Harmonic L2 | 30104 | 0.1 | % | int16 | R
3rd Harmonic L3 | 30005 | 0.1 | % | int16 | R | 2nd Harmonic L3 | 30105 | 0.1 | % | int16 | R
5th Harmonic L1 | 30006 | 0.1 | % | int16 | R | 4th Harmonic L1 | 30106 | 0.1 | % | int16 | R
5th Harmonic L2 | 30007 | 0.1 | % | int16 | R | 4th Harmonic L2 | 30107 | 0.1 | % | int16 | R
5th Harmonic L3 | 30008 | 0.1 | % | int16 | R | 4th Harmonic L3 | 30108 | 0.1 | % | int16 | R
7th Harmonic L1 | 30009 | 0.1 | % | int16 | R | 6th Harmonic L1 | 30109 | 0.1 | % | int16 | R
7th Harmonic L2 | 30010 | 0.1 | % | int16 | R | 6th Harmonic L2 | 30110 | 0.1 | % | int16 | R
7th Harmonic L3 | 30011 | 0.1 | % | int16 | R | 6th Harmonic L3 | 30111 | 0.1 | % | int16 | R
9th Harmonic L1 | 30012 | 0.1 | % | int16 | R | 8th Harmonic L1 | 30112 | 0.1 | % | int16 | R
9th Harmonic L2 | 30013 | 0.1 | % | int16 | R | 8th Harmonic L2 | 30113 | 0.1 | % | int16 | R
9th Harmonic L3 | 30014 | 0.1 | % | int16 | R | 8th Harmonic L3 | 30114 | 0.1 | % | int16 | R
11th Harmonic L1 | 30015 | 0.1 | % | int16 | R | 10th Harmonic L1 | 30115 | 0.1 | % | int16 | R
11th Harmonic L2 | 30016 | 0.1 | % | int16 | R | 10th Harmonic L2 | 30116 | 0.1 | % | int16 | R
11th Harmonic L3 | 30017 | 0.1 | % | int16 | R | 10th Harmonic L3 | 30117 | 0.1 | % | int16 | R
13th Harmonic L1 | 30018 | 0.1 | % | int16 | R | 12th Harmonic L1 | 30118 | 0.1 | % | int16 | R
13th Harmonic L2 | 30019 | 0.1 | % | int16 | R | 12th Harmonic L2 | 30119 | 0.1 | % | int16 | R
13th Harmonic L3 | 30020 | 0.1 | % | int16 | R | 12th Harmonic L3 | 30120 | 0.1 | % | int16 | R
15th Harmonic L1 | 30021 | 0.1 | % | int16 | R | 14th Harmonic L1 | 30121 | 0.1 | % | int16 | R
15th Harmonic L2 | 30022 | 0.1 | % | int16 | R | 14th Harmonic L2 | 30122 | 0.1 | % | int16 | R
15th Harmonic L3 | 30023 | 0.1 | % | int16 | R | 14th Harmonic L3 | 30123 | 0.1 | % | int16 | R
17th Harmonic L1 | 30024 | 0.1 | % | int16 | R | 16th Harmonic L1 | 30124 | 0.1 | % | int16 | R
17th Harmonic L2 | 30025 | 0.1 | % | int16 | R | 16th Harmonic L2 | 30125 | 0.1 | % | int16 | R
17th Harmonic L3 | 30026 | 0.1 | % | int16 | R | 16th Harmonic L3 | 30126 | 0.1 | % | int16 | R
19th Harmonic L1 | 30027 | 0.1 | % | int16 | R | 18th Harmonic L1 | 30127 | 0.1 | % | int16 | R
19th Harmonic L2 | 30028 | 0.1 | % | int16 | R | 18th Harmonic L2 | 30128 | 0.1 | % | int16 | R
19th Harmonic L3 | 30029 | 0.1 | % | int16 | R | 18th Harmonic L3 | 30129 | 0.1 | % | int16 | R
21st Harmonic L1 | 30030 | 0.1 | % | int16 | R | 20th Harmonic L1 | 30130 | 0.1 | % | int16 | R
21st Harmonic L2 | 30031 | 0.1 | % | int16 | R | 20th Harmonic L2 | 30131 | 0.1 | % | int16 | R
21st Harmonic L3 | 30032 | 0.1 | % | int16 | R | 20th Harmonic L3 | 30132 | 0.1 | % | int16 | R
23rd Harmonic L1 | 30033 | 0.1 | % | int16 | R | 22nd Harmonic L1 | 30133 | 0.1 | % | int16 | R
23rd Harmonic L2 | 30034 | 0.1 | % | int16 | R | 22nd Harmonic L2 | 30134 | 0.1 | % | int16 | R
23rd Harmonic L3 | 30035 | 0.1 | % | int16 | R | 22nd Harmonic L3 | 30135 | 0.1 | % | int16 | R
25th Harmonic L1 | 30036 | 0.1 | % | int16 | R | 24th Harmonic L1 | 30136 | 0.1 | % | int16 | R
25th Harmonic L2 | 30037 | 0.1 | % | int16 | R | 24th Harmonic L2 | 30137 | 0.1 | % | int16 | R
25th Harmonic L3 | 30038 | 0.1 | % | int16 | R | 24th Harmonic L3 | 30138 | 0.1 | % | int16 | R
27th Harmonic L1 | 30039 | 0.1 | % | int16 | R | 26th Harmonic L1 | 30139 | 0.1 | % | int16 | R
27th Harmonic L2 | 30040 | 0.1 | % | int16 | R | 26th Harmonic L2 | 30140 | 0.1 | % | int16 | R
27th Harmonic L3 | 30041 | 0.1 | % | int16 | R | 26th Harmonic L3 | 30141 | 0.1 | % | int16 | R
29th Harmonic L1 | 30042 | 0.1 | % | int16 | R | 28th Harmonic L1 | 30142 | 0.1 | % | int16 | R
29th Harmonic L2 | 30043 | 0.1 | % | int16 | R | 28th Harmonic L2 | 30143 | 0.1 | % | int16 | R
29th Harmonic L3 | 30044 | 0.1 | % | int16 | R | 28th Harmonic L3 | 30144 | 0.1 | % | int16 | R
31st Harmonic L1 | 30045 | 0.1 | % | int16 | R | 30th Harmonic L1 | 30145 | 0.1 | % | int16 | R
31st Harmonic L2 | 30046 | 0.1 | % | int16 | R | 30th Harmonic L2 | 30146 | 0.1 | % | int16 | R
31st Harmonic L3 | 30047 | 0.1 | % | int16 | R | 30th Harmonic L3 | 30147 | 0.1 | % | int16 | R
33rd Harmonic L1 | 30048 | 0.1 | % | int16 | R | 32nd Harmonic L1 | 30148 | 0.1 | % | int16 | R
33rd Harmonic L2 | 30049 | 0.1 | % | int16 | R | 32nd Harmonic L2 | 30149 | 0.1 | % | int16 | R
33rd Harmonic L3 | 30050 | 0.1 | % | int16 | R | 32nd Harmonic L3 | 30150 | 0.1 | % | int16 | R
35th Harmonic L1 | 30051 | 0.1 | % | int16 | R | 34th Harmonic L1 | 30151 | 0.1 | % | int16 | R
35th Harmonic L2 | 30052 | 0.1 | % | int16 | R | 34th Harmonic L2 | 30152 | 0.1 | % | int16 | R
35th Harmonic L3 | 30053 | 0.1 | % | int16 | R | 34th Harmonic L3 | 30153 | 0.1 | % | int16 | R
37th Harmonic L1 | 30054 | 0.1 | % | int16 | R | 36th Harmonic L1 | 30154 | 0.1 | % | int16 | R
37th Harmonic L2 | 30055 | 0.1 | % | int16 | R | 36th Harmonic L2 | 30155 | 0.1 | % | int16 | R
37th Harmonic L3 | 30056 | 0.1 | % | int16 | R | 36th Harmonic L3 | 30156 | 0.1 | % | int16 | R
39th Harmonic L1 | 30057 | 0.1 | % | int16 | R | 38th Harmonic L1 | 30157 | 0.1 | % | int16 | R
39th Harmonic L2 | 30058 | 0.1 | % | int16 | R | 38th Harmonic L2 | 30158 | 0.1 | % | int16 | R
39th Harmonic L3 | 30059 | 0.1 | % | int16 | R | 38th Harmonic L3 | 30159 | 0.1 | % | int16 | R
41st Harmonic L1 | 30060 | 0.1 | % | int16 | R | 40th Harmonic L1 | 30160 | 0.1 | % | int16 | R
41st Harmonic L2 | 30061 | 0.1 | % | int16 | R | 40th Harmonic L2 | 30161 | 0.1 | % | int16 | R
41st Harmonic L3 | 30062 | 0.1 | % | int16 | R | 40th Harmonic L3 | 30162 | 0.1 | % | int16 | R
43rd Harmonic L1 | 30063 | 0.1 | % | int16 | R | 42nd Harmonic L1 | 30163 | 0.1 | % | int16 | R
43rd Harmonic L2 | 30064 | 0.1 | % | int16 | R | 42nd Harmonic L2 | 30164 | 0.1 | % | int16 | R
43rd Harmonic L3 | 30065 | 0.1 | % | int16 | R | 42nd Harmonic L3 | 30165 | 0.1 | % | int16 | R
45th Harmonic L1 | 30066 | 0.1 | % | int16 | R | 44th Harmonic L1 | 30166 | 0.1 | % | int16 | R
45th Harmonic L2 | 30067 | 0.1 | % | int16 | R | 44th Harmonic L2 | 30167 | 0.1 | % | int16 | R
45th Harmonic L3 | 30068 | 0.1 | % | int16 | R | 44th Harmonic L3 | 30168 | 0.1 | % | int16 | R
47th Harmonic L1 | 30069 | 0.1 | % | int16 | R | 46th Harmonic L1 | 30169 | 0.1 | % | int16 | R
47th Harmonic L2 | 30070 | 0.1 | % | int16 | R | 46th Harmonic L2 | 30170 | 0.1 | % | int16 | R
47th Harmonic L3 | 30071 | 0.1 | % | int16 | R | 46th Harmonic L3 | 30171 | 0.1 | % | int16 | R
49th Harmonic L1 | 30072 | 0.1 | % | int16 | R | 48th Harmonic L1 | 30172 | 0.1 | % | int16 | R
49th Harmonic L2 | 30073 | 0.1 | % | int16 | R | 48th Harmonic L2 | 30173 | 0.1 | % | int16 | R
49th Harmonic L3 | 30074 | 0.1 | % | int16 | R | 48th Harmonic L3 | 30174 | 0.1 | % | int16 | R
51st Harmonic L1 | 30075 | 0.1 | % | int16 | R | 50th Harmonic L1 | 30175 | 0.1 | % | int16 | R
51st Harmonic L2 | 30076 | 0.1 | % | int16 | R | 50th Harmonic L2 | 30176 | 0.1 | % | int16 | R
51st Harmonic L3 | 30077 | 0.1 | % | int16 | R | 50th Harmonic L3 | 30177 | 0.1 | % | int16 | R
53rd Harmonic L1 | 30078 | 0.1 | % | int16 | R | 52nd Harmonic L1 | 30178 | 0.1 | % | int16 | R
53rd Harmonic L2 | 30079 | 0.1 | % | int16 | R | 52nd Harmonic L2 | 30179 | 0.1 | % | int16 | R
53rd Harmonic L3 | 30080 | 0.1 | % | int16 | R | 52nd Harmonic L3 | 30180 | 0.1 | % | int16 | R
55th Harmonic L1 | 30081 | 0.1 | % | int16 | R | 54th Harmonic L1 | 30181 | 0.1 | % | int16 | R
55th Harmonic L2 | 30082 | 0.1 | % | int16 | R | 54th Harmonic L2 | 30182 | 0.1 | % | int16 | R
55th Harmonic L3 | 30083 | 0.1 | % | int16 | R | 54th Harmonic L3 | 30183 | 0.1 | % | int16 | R
57th Harmonic L1 | 30084 | 0.1 | % | int16 | R | 56th Harmonic L1 | 30184 | 0.1 | % | int16 | R
57th Harmonic L2 | 30085 | 0.1 | % | int16 | R | 56th Harmonic L2 | 30185 | 0.1 | % | int16 | R
57th Harmonic L3 | 30086 | 0.1 | % | int16 | R | 56th Harmonic L3 | 30186 | 0.1 | % | int16 | R
59th Harmonic L1 | 30087 | 0.1 | % | int16 | R | 58th Harmonic L1 | 30187 | 0.1 | % | int16 | R
59th Harmonic L2 | 30088 | 0.1 | % | int16 | R | 58th Harmonic L2 | 30188 | 0.1 | % | int16 | R
59th Harmonic L3 | 30089 | 0.1 | % | int16 | R | 58th Harmonic L3 | 30189 | 0.1 | % | int16 | R
61st Harmonic L1 | 30090 | 0.1 | % | int16 | R | 60th Harmonic L1 | 30190 | 0.1 | % | int16 | R
61st Harmonic L2 | 30091 | 0.1 | % | int16 | R | 60th Harmonic L2 | 30191 | 0.1 | % | int16 | R
61st Harmonic L3 | 30092 | 0.1 | % | int16 | R | 60th Harmonic L3 | 30192 | 0.1 | % | int16 | R
63rd Harmonic L1 | 30093 | 0.1 | % | int16 | R | 62nd Harmonic L1 | 30193 | 0.1 | % | int16 | R
63rd Harmonic L2 | 30094 | 0.1 | % | int16 | R | 62nd Harmonic L2 | 30194 | 0.1 | % | int16 | R
63rd Harmonic L3 | 30095 | 0.1 | % | int16 | R | 62nd Harmonic L3 | 30195 | 0.1 | % | int16 | R
Current Harmonic RMS (Odd) | Adress | Multiplier | Index | Type | W/R | Current Harmonic RMS (Even) | Adress | Multiplier | Index | Type | W/R
Odd/Even Profile | 30246 | - |  | int32 | R | Odd/Even Profile | 30496 | - |  | int32 | R
Harmonic Limit | 30248 | - |  | int32 | R | Harmonic Limit | 30498 | - |  | int32 | R
1. Phase Fundamental Component | 30250 | 1 | % | int32 | R | 1. Phase Fundamental Component | 30500 | 1 | % | int32 | R
2. Phase Fundamental Component | 30252 | 1 | % | int32 | R | 2. Phase Fundamental Component | 30502 | 1 | % | int32 | R
3. Phase Fundamental Component | 30254 | 1 | % | int32 | R | 3. Phase Fundamental Component | 30504 | 1 | % | int32 | R
3rd Harmonic L1 | 30256 | 1 | % | int32 | R | 2nd Harmonic L1 | 30506 | 1 | % | int32 | R
3rd Harmonic L2 | 30258 | 1 | % | int32 | R | 2nd Harmonic L2 | 30508 | 1 | % | int32 | R
3rd Harmonic L3 | 30260 | 1 | % | int32 | R | 2nd Harmonic L3 | 30510 | 1 | % | int32 | R
5th Harmonic L1 | 30262 | 1 | % | int32 | R | 4th Harmonic L1 | 30512 | 1 | % | int32 | R
5th Harmonic L2 | 30264 | 1 | % | int32 | R | 4th Harmonic L2 | 30514 | 1 | % | int32 | R
5th Harmonic L3 | 30266 | 1 | % | int32 | R | 4th Harmonic L3 | 30516 | 1 | % | int32 | R
7th Harmonic L1 | 30268 | 1 | % | int32 | R | 6th Harmonic L1 | 30518 | 1 | % | int32 | R
7th Harmonic L2 | 30270 | 1 | % | int32 | R | 6th Harmonic L2 | 30520 | 1 | % | int32 | R
7th Harmonic L3 | 30272 | 1 | % | int32 | R | 6th Harmonic L3 | 30522 | 1 | % | int32 | R
9th Harmonic L1 | 30274 | 1 | % | int32 | R | 8th Harmonic L1 | 30524 | 1 | % | int32 | R
9th Harmonic L2 | 30276 | 1 | % | int32 | R | 8th Harmonic L2 | 30526 | 1 | % | int32 | R
9th Harmonic L3 | 30278 | 1 | % | int32 | R | 8th Harmonic L3 | 30528 | 1 | % | int32 | R
11th Harmonic L1 | 30280 | 1 | % | int32 | R | 10th Harmonic L1 | 30530 | 1 | % | int32 | R
11th Harmonic L2 | 30282 | 1 | % | int32 | R | 10th Harmonic L2 | 30532 | 1 | % | int32 | R
11th Harmonic L3 | 30284 | 1 | % | int32 | R | 10th Harmonic L3 | 30534 | 1 | % | int32 | R
13th Harmonic L1 | 30286 | 1 | % | int32 | R | 12th Harmonic L1 | 30536 | 1 | % | int32 | R
13th Harmonic L2 | 30288 | 1 | % | int32 | R | 12th Harmonic L2 | 30538 | 1 | % | int32 | R
13th Harmonic L3 | 30290 | 1 | % | int32 | R | 12th Harmonic L3 | 30540 | 1 | % | int32 | R
15th Harmonic L1 | 30292 | 1 | % | int32 | R | 14th Harmonic L1 | 30542 | 1 | % | int32 | R
15th Harmonic L2 | 30294 | 1 | % | int32 | R | 14th Harmonic L2 | 30544 | 1 | % | int32 | R
15th Harmonic L3 | 30296 | 1 | % | int32 | R | 14th Harmonic L3 | 30546 | 1 | % | int32 | R
17th Harmonic L1 | 30298 | 1 | % | int32 | R | 16th Harmonic L1 | 30548 | 1 | % | int32 | R
17th Harmonic L2 | 30300 | 1 | % | int32 | R | 16th Harmonic L2 | 30550 | 1 | % | int32 | R
17th Harmonic L3 | 30302 | 1 | % | int32 | R | 16th Harmonic L3 | 30552 | 1 | % | int32 | R
19th Harmonic L1 | 30304 | 1 | % | int32 | R | 18th Harmonic L1 | 30554 | 1 | % | int32 | R
19th Harmonic L2 | 30306 | 1 | % | int32 | R | 18th Harmonic L2 | 30556 | 1 | % | int32 | R
19th Harmonic L3 | 30308 | 1 | % | int32 | R | 18th Harmonic L3 | 30558 | 1 | % | int32 | R
21st Harmonic L1 | 30310 | 1 | % | int32 | R | 20th Harmonic L1 | 30560 | 1 | % | int32 | R
21st Harmonic L2 | 30312 | 1 | % | int32 | R | 20th Harmonic L2 | 30562 | 1 | % | int32 | R
21st Harmonic L3 | 30314 | 1 | % | int32 | R | 20th Harmonic L3 | 30564 | 1 | % | int32 | R
23rd Harmonic L1 | 30316 | 1 | % | int32 | R | 22nd Harmonic L1 | 30566 | 1 | % | int32 | R
23rd Harmonic L2 | 30318 | 1 | % | int32 | R | 22nd Harmonic L2 | 30568 | 1 | % | int32 | R
23rd Harmonic L3 | 30320 | 1 | % | int32 | R | 22nd Harmonic L3 | 30570 | 1 | % | int32 | R
25th Harmonic L1 | 30322 | 1 | % | int32 | R | 24th Harmonic L1 | 30572 | 1 | % | int32 | R
25th Harmonic L2 | 30324 | 1 | % | int32 | R | 24th Harmonic L2 | 30574 | 1 | % | int32 | R
25th Harmonic L3 | 30326 | 1 | % | int32 | R | 24th Harmonic L3 | 30576 | 1 | % | int32 | R
27th Harmonic L1 | 30328 | 1 | % | int32 | R | 26th Harmonic L1 | 30578 | 1 | % | int32 | R
27th Harmonic L2 | 30330 | 1 | % | int32 | R | 26th Harmonic L2 | 30580 | 1 | % | int32 | R
27th Harmonic L3 | 30332 | 1 | % | int32 | R | 26th Harmonic L3 | 30582 | 1 | % | int32 | R
29th Harmonic L1 | 30334 | 1 | % | int32 | R | 28th Harmonic L1 | 30584 | 1 | % | int32 | R
29th Harmonic L2 | 30336 | 1 | % | int32 | R | 28th Harmonic L2 | 30586 | 1 | % | int32 | R
29th Harmonic L3 | 30338 | 1 | % | int32 | R | 28th Harmonic L3 | 30588 | 1 | % | int32 | R
31st Harmonic L1 | 30340 | 1 | % | int32 | R | 30th Harmonic L1 | 30590 | 1 | % | int32 | R
31st Harmonic L2 | 30342 | 1 | % | int32 | R | 30th Harmonic L2 | 30592 | 1 | % | int32 | R
31st Harmonic L3 | 30344 | 1 | % | int32 | R | 30th Harmonic L3 | 30594 | 1 | % | int32 | R
33rd Harmonic L1 | 30346 | 1 | % | int32 | R | 32nd Harmonic L1 | 30596 | 1 | % | int32 | R
33rd Harmonic L2 | 30348 | 1 | % | int32 | R | 32nd Harmonic L2 | 30598 | 1 | % | int32 | R
33rd Harmonic L3 | 30350 | 1 | % | int32 | R | 32nd Harmonic L3 | 30600 | 1 | % | int32 | R
35th Harmonic L1 | 30352 | 1 | % | int32 | R | 34th Harmonic L1 | 30602 | 1 | % | int32 | R
35th Harmonic L2 | 30354 | 1 | % | int32 | R | 34th Harmonic L2 | 30604 | 1 | % | int32 | R
35th Harmonic L3 | 30356 | 1 | % | int32 | R | 34th Harmonic L3 | 30606 | 1 | % | int32 | R
37th Harmonic L1 | 30358 | 1 | % | int32 | R | 36th Harmonic L1 | 30608 | 1 | % | int32 | R
37th Harmonic L2 | 30360 | 1 | % | int32 | R | 36th Harmonic L2 | 30610 | 1 | % | int32 | R
37th Harmonic L3 | 30362 | 1 | % | int32 | R | 36th Harmonic L3 | 30612 | 1 | % | int32 | R
39th Harmonic L1 | 30364 | 1 | % | int32 | R | 38th Harmonic L1 | 30614 | 1 | % | int32 | R
39th Harmonic L2 | 30366 | 1 | % | int32 | R | 38th Harmonic L2 | 30616 | 1 | % | int32 | R
39th Harmonic L3 | 30368 | 1 | % | int32 | R | 38th Harmonic L3 | 30618 | 1 | % | int32 | R
41st Harmonic L1 | 30370 | 1 | % | int32 | R | 40th Harmonic L1 | 30620 | 1 | % | int32 | R
41st Harmonic L2 | 30372 | 1 | % | int32 | R | 40th Harmonic L2 | 30622 | 1 | % | int32 | R
41st Harmonic L3 | 30374 | 1 | % | int32 | R | 40th Harmonic L3 | 30624 | 1 | % | int32 | R
43rd Harmonic L1 | 30376 | 1 | % | int32 | R | 42nd Harmonic L1 | 30626 | 1 | % | int32 | R
43rd Harmonic L2 | 30378 | 1 | % | int32 | R | 42nd Harmonic L2 | 30628 | 1 | % | int32 | R
43rd Harmonic L3 | 30380 | 1 | % | int32 | R | 42nd Harmonic L3 | 30630 | 1 | % | int32 | R
45th Harmonic L1 | 30382 | 1 | % | int32 | R | 44th Harmonic L1 | 30632 | 1 | % | int32 | R
45th Harmonic L2 | 30384 | 1 | % | int32 | R | 44th Harmonic L2 | 30634 | 1 | % | int32 | R
45th Harmonic L3 | 30386 | 1 | % | int32 | R | 44th Harmonic L3 | 30636 | 1 | % | int32 | R
47th Harmonic L1 | 30388 | 1 | % | int32 | R | 46th Harmonic L1 | 30638 | 1 | % | int32 | R
47th Harmonic L2 | 30390 | 1 | % | int32 | R | 46th Harmonic L2 | 30640 | 1 | % | int32 | R
47th Harmonic L3 | 30392 | 1 | % | int32 | R | 46th Harmonic L3 | 30642 | 1 | % | int32 | R
49th Harmonic L1 | 30394 | 1 | % | int32 | R | 48th Harmonic L1 | 30644 | 1 | % | int32 | R
49th Harmonic L2 | 30396 | 1 | % | int32 | R | 48th Harmonic L2 | 30646 | 1 | % | int32 | R
49th Harmonic L3 | 30398 | 1 | % | int32 | R | 48th Harmonic L3 | 30648 | 1 | % | int32 | R
51st Harmonic L1 | 30400 | 1 | % | int32 | R | 50th Harmonic L1 | 30650 | 1 | % | int32 | R
51st Harmonic L2 | 30402 | 1 | % | int32 | R | 50th Harmonic L2 | 30652 | 1 | % | int32 | R
51st Harmonic L3 | 30404 | 1 | % | int32 | R | 50th Harmonic L3 | 30654 | 1 | % | int32 | R
53rd Harmonic L1 | 30406 | 1 | % | int32 | R | 52nd Harmonic L1 | 30656 | 1 | % | int32 | R
53rd Harmonic L2 | 30408 | 1 | % | int32 | R | 52nd Harmonic L2 | 30658 | 1 | % | int32 | R
53rd Harmonic L3 | 30410 | 1 | % | int32 | R | 52nd Harmonic L3 | 30660 | 1 | % | int32 | R
55th Harmonic L1 | 30412 | 1 | % | int32 | R | 54th Harmonic L1 | 30662 | 1 | % | int32 | R
55th Harmonic L2 | 30414 | 1 | % | int32 | R | 54th Harmonic L2 | 30664 | 1 | % | int32 | R
55th Harmonic L3 | 30416 | 1 | % | int32 | R | 54th Harmonic L3 | 30666 | 1 | % | int32 | R
57th Harmonic L1 | 30418 | 1 | % | int32 | R | 56th Harmonic L1 | 30668 | 1 | % | int32 | R
57th Harmonic L2 | 30420 | 1 | % | int32 | R | 56th Harmonic L2 | 30670 | 1 | % | int32 | R
57th Harmonic L3 | 30422 | 1 | % | int32 | R | 56th Harmonic L3 | 30672 | 1 | % | int32 | R
59th Harmonic L1 | 30424 | 1 | % | int32 | R | 58th Harmonic L1 | 30674 | 1 | % | int32 | R
59th Harmonic L2 | 30426 | 1 | % | int32 | R | 58th Harmonic L2 | 30676 | 1 | % | int32 | R
59th Harmonic L3 | 30428 | 1 | % | int32 | R | 58th Harmonic L3 | 30678 | 1 | % | int32 | R
61st Harmonic L1 | 30430 | 1 | % | int32 | R | 60th Harmonic L1 | 30680 | 1 | % | int32 | R
61st Harmonic L2 | 30432 | 1 | % | int32 | R | 60th Harmonic L2 | 30682 | 1 | % | int32 | R
61st Harmonic L3 | 30434 | 1 | % | int32 | R | 60th Harmonic L3 | 30684 | 1 | % | int32 | R
63rd Harmonic L1 | 30436 | 1 | % | int32 | R | 62nd Harmonic L1 | 30686 | 1 | % | int32 | R
63rd Harmonic L2 | 30438 | 1 | % | int32 | R | 62nd Harmonic L2 | 30688 | 1 | % | int32 | R
63rd Harmonic L3 | 30440 | 1 | % | int32 | R | 62nd Harmonic L3 | 30690 | 1 | % | int32 | R

## Ratios
Ratio | Adress | Multiplier | Unit | Size | W/R
Instantaneous | 14000 | 0.1 |  | int16 | R
Instantaneous | 14001 | 0.1 |  | int16 | R
Instantaneous | 14002 | 0.1 |  | int16 | R
Instantaneous | 14003 | 0.1 |  | int16 | R
Instantaneous | 14004 | 0.1 |  | int16 | R
Instantaneous | 14005 | 0.1 |  | int16 | R
Instantaneous | 14006 | 0.1 |  | int16 | R
Instantaneous | 14007 | 0.1 |  | int16 | R
1. Phase Inductive Ratio (Import) | 14008 | 0.1 | % | int16 | R
2. Phase Inductive Ratio (Import) | 14009 | 0.1 | % | int16 | R
3. Phase Inductive Ratio (Import) | 14010 | 0.1 | % | int16 | R
Total Inductive Ratio (Import) | 14011 | 0.1 | % | int16 | R
1. Phase Capacitive Ratio (Import) | 14012 | 0.1 | % | int16 | R
2. Phase Capacitive Ratio (Import) | 14013 | 0.1 | % | int16 | R
3. Phase Capacitive Ratio (Import) | 14014 | 0.1 | % | int16 | R
Total Capacitive Ratio (Import) | 14015 | 0.1 | % | int16 | R
Instantaneous | 14050 | 0.1 |  | int16 | R
Instantaneous | 14051 | 0.1 |  | int16 | R
Instantaneous | 14052 | 0.1 |  | int16 | R
Instantaneous | 14053 | 0.1 |  | int16 | R
Instantaneous | 14054 | 0.1 |  | int16 | R
Instantaneous | 14055 | 0.1 |  | int16 | R
Instantaneous | 14056 | 0.1 |  | int16 | R
Instantaneous | 14057 | 0.1 |  | int16 | R
1. Phase Inductive Ratio (Export) | 14058 | 0.1 | % | int16 | R
2. Phase Inductive Ratio (Export) | 14059 | 0.1 | % | int16 | R
3. Phase Inductive Ratio (Export) | 14060 | 0.1 | % | int16 | R
Total Inductive Ratio (Export) | 14061 | 0.1 | % | int16 | R
1. Phase Capacitive Ratio (Export) | 14062 | 0.1 | % | int16 | R
2. Phase Capacitive Ratio (Export) | 14063 | 0.1 | % | int16 | R
3. Phase Capacitive Ratio (Export) | 14064 | 0.1 | % | int16 | R
Total Capacitive Ratio (Export) | 14065 | 0.1 | % | int16 | R

## Alarms
Events (Number of Occurrences) | [5 empty] | Warnings (Number of Occurrences) | [6 empty] | System Errors (Number of Occurrences)
Alarm Name | Adress | Multiplier | Unit | Type | W/R | Alarm Name | Adress | Multiplier | Unit | Type | W/R |  | Alarm Name | Adress | Multiplier | Unit | Type | W/R
Low Voltage L1 | 47000 | - | - | int 16 | R | Current Overload / Current Overflow | 48000 | - | - | int 16 | R |  | Reset, Tick Full | 49000 | - | - | int 16 | R
Low Voltage L2 | 47001 | - | - | int 16 | R | Overcurrent L1 | 48001 | - | - | int 16 | R |  | Reset, Exception Status | 49001 | - | - | int 16 | R
Low Voltage L3 | 47002 | - | - | int 16 | R | Overcurrent L2 | 48002 | - | - | int 16 | R |  | Reset, Insufficient Resource | 49002 | - | - | int 16 | R
Missing Phase Terminal | 47003 | - | - | int 16 | R | Overcurrent L3 | 48003 | - | - | int 16 | R |  | Reset, Message Queue Full | 49003 | - | - | int 16 | R
No Voltage L1 | 47004 | - | - | int 16 | R | Low Voltage L1 | 48004 | - | - | int 16 | R |  | Safe Reset-1 | 49005 | - | - | int 16 | R
No Voltage L2 | 47005 | - | - | int 16 | R | Low Voltage L2 | 48005 | - | - | int 16 | R |  | Safe Reset-2 | 49006 | - | - | int 16 | R
No Voltage L3 | 47006 | - | - | int 16 | R | Low Voltage L3 | 48006 | - | - | int 16 | R |  | Safe Reset-3 | 49007 | - | - | int 16 | R
Energies Cleared | 47007 | - | - | int 16 | R | Overvoltage L1 | 48007 | - | - | int 16 | R |  | Reset, Quality Test | 49008 | - | - | int 16 | R
Min Max Cleared | 47008 | - | - | int 16 | R | Overvoltage L2 | 48008 | - | - | int 16 | R |  | Safe Reset-4 | 49009 | - | - | int 16 | R
Demands Cleared | 47009 | - | - | int 16 | R | Overvoltage L3 | 48009 | - | - | int 16 | R |  | Reset, Service Out | 49010 | - | - | int 16 | R
Ratios Cleared | 47010 | - | - | int 16 | R | Over-Inductive | 48010 | - | - | int 16 | R |  | Reset, Non-Maskable | 49011 | - | - | int 16 | R
RGP Cleared | 47011 | - | - | int 16 | R | Over-Capacitive | 48011 | - | - | int 16 | R |  | Safe Reset-5 | 49012 | - | - | int 16 | R
RGP Compressed | 47012 | - | - | int 16 | R | C.T. Ratio Error | 48012 | - | - | int 16 | R |  | Safe Reset-6 | 49013 | - | - | int 16 | R
Invalid PIN | 47013 | - | - | int 16 | R | C.T. Direction Changed | 48013 | - | - | int 16 | R |  | Reset, Modbus | 49014 | - | - | int 16 | R
PIN Changed | 47014 | - | - | int 16 | R | RTC Error | 48016 | - | - | int 16 | R |  | Reset, Forced | 49015 | - | - | int 16 | R
Special PIN Entered | 47015 | - | - | int 16 | R | SD Card Memory Full | 48017 | - | - | int 16 | R |  | Reset, SD-USB Formatting | 49016 | - | - | int 16 | R
PIN Tampering | 47016 | - | - | int 16 | R | SD Card Connection Failed | 48018 | - | - | int 16 | R |  | FatFS Write Skipped | 49017 | - | - | int 16 | R
Factory Settings | 47017 | - | - | int 16 | R | SD Card Records Cleared | 48019 | - | - | int 16 | R |  | Reset, Menu | 49018 | - | - | int 16 | R
Long Integration Time | 47019 | - | - | int 16 | R | SD Card Records Could Not Be Cleared | 48020 | - | - | int 16 | R |  | Reset, PC Command | 49019 | - | - | int 16 | R
Device Powered On | 47020 | - | - | int 16 | R | SD Card Formatted | 48021 | - | - | int 16 | R |  | Safe Reset-7 | 49020 | - | - | int 16 | R
Device Powered Off | 47021 | - | - | int 16 | R | SD Card Could Not Be Formatted | 48022 | - | - | int 16 | R |  | Safe Reset-8 | 49021 | - | - | int 16 | R
Date/Time Updated | 47022 | - | - | int 16 | R | SD Card Connection Lost | 48023 | - | - | int 16 | R |  | Reset, Default Settings | 49022 | - | - | int 16 | R
Date/Time Changed | 47023 | - | - | int 16 | R | SD Card Recording Ended | 48024 | - | - | int 16 | R |  | RTC Read Error | 49023 | - | - | int 16 | R
Date/Time Changed Remotely | 47024 | - | - | int 16 | R | USB Memory Full | 48025 | - | - | int 16 | R |  | RTC Write Error 1 | 49024 | - | - | int 16 | R
Language Changed | 47025 | - | - | int 16 | R | USB Connection Failed | 48026 | - | - | int 16 | R |  | RTC Write Error 2 | 49025 | - | - | int 16 | R
Short Power Interruption | 47026 | - | - | int 16 | R | USB Records Cleared | 48027 | - | - | int 16 | R |  | RTC Crystal Error | 49026 | - | - | int 16 | R
Grid Frequency Changed | 47027 | - | - | int 16 | R | USB Records Could Not Be Cleared | 48028 | - | - | int 16 | R |  | RTC Battery Error | 49027 | - | - | int 16 | R
Auto Grid Frequency | 47028 | - | - | int 16 | R | USB Formatted | 48029 | - | - | int 16 | R |  | RTC Enter Init Error | 49028 | - | - | int 16 | R
Pulse Output Counter Reset | 47037 | - | - | int 16 | R | USB Could Not Be Formatted | 48030 | - | - | int 16 | R |  | RTC Exit Init Error | 49029 | - | - | int 16 | R
Input-1 Trigger Counter Reset | 47038 | - | - | int 16 | R | USB Connection Lost | 48031 | - | - | int 16 | R |  | RTC Backup Reg Error | 49030 | - | - | int 16 | R
Input-1 Pulse Counter Reset | 47039 | - | - | int 16 | R | USB Recording Ended | 48032 | - | - | int 16 | R |  | RTC Backup Read Error | 49031 | - | - | int 16 | R
Input-2 Trigger Counter Reset | 47040 | - | - | int 16 | R | Pulse Index Value Low | 48033 | - | - | int 16 | R |  | RTC Sync Error | 49032 | - | - | int 16 | R
Input-2 Pulse Counter Reset | 47041 | - | - | int 16 | R | Over-Harmonic | 48034 | - | - | int 16 | R |  | Device Reset Error | 49034 | - | - | int 16 | R
Modbus Parity Error | 47042 | - | - | int 16 | R | Over-Harmonic L1 | 48035 | - | - | int 16 | R |  | Power Interruption HW Error | 49035 | - | - | int 16 | R
Line Current Normalized | 47046 | - | - | int 16 | R | Over-Harmonic L2 | 48036 | - | - | int 16 | R |  | Memory Value Inverted | 49038 | - | - | int 16 | R
L1 Voltage Normalized | 47047 | - | - | int 16 | R | Over-Harmonic L3 | 48037 | - | - | int 16 | R |  | External Crystal Error | 49039 | - | - | int 16 | R
L2 Voltage Normalized | 47048 | - | - | int 16 | R | Overtemperature | 48038 | - | - | int 16 | R |  | Memory Reset Write | 49040 | - | - | int 16 | R
L3 Voltage Normalized | 47049 | - | - | int 16 | R | Modbus Access Denied | 48039 | - | - | int 16 | R |  | Memory Signature | 49041 | - | - | int 16 | R
Temperature Normalized | 47050 | - | - | int 16 | R | RGP Table Full | 48040 | - | - | int 16 | R |  | Memory Corrected | 49042 | - | - | int 16 | R
SMPS Voltage Normalized | 47051 | - | - | int 16 | R | RTC Recovered | 48041 | - | - | int 16 | R |  | Memory Invalid | 49043 | - | - | int 16 | R
L1 Harmonic Normalized | 47052 | - | - | int 16 | R | C.T. Ratio Changed | 48042 | - | - | int 16 | R |  | Memory Write Prm. (Parameters) | 49044 | - | - | int 16 | R
L2 Harmonic Normalized | 47053 | - | - | int 16 | R | V.T. Ratio Changed | 48043 | - | - | int 16 | R |  | Memory Write Demand | 49046 | - | - | int 16 | R
L3 Harmonic Normalized | 47054 | - | - | int 16 | R | [7 empty] | Memory Write Energy | 49047 | - | - | int 16 | R
Maintenance Mode Enabled | 47058 | - | - | int 16 | R | [7 empty] | Memory Write RGP | 49048 | - | - | int 16 | R
Maintenance Mode Disabled | 47059 | - | - | int 16 | R | Koruma, Aşırı Gerilim L2 | [6 empty] | Memory Write MinMax | 49049 | - | - | int 16 | R
Maintenance Time Reached | 47060 | - | - | int 16 | R | Warnings (Date of Creation) | [6 empty] | Memory Read Prm. (Parameters) | 49052 | - | - | int 16 | R
Modbus Address Changed | 47061 | - | - | int 16 | R | Alarm Name | Adress | Multiplier | Unit | Type | W/R | W/R | Memory Read Alarm | 49053 | - | - | int 16 | R
Modbus Speed Changed | 47062 | - | - | int 16 | R | Current Overflow | 51000 | 54000 | - | - | int 32 | R | Memory Read Demand | 49054 | - | - | int 16 | R
Modbus Settings Changed | 47063 | - | - | int 16 | R | Overcurrent L1 | 51002 | 54002 | - | - | int 32 | R | Memory Read Energy | 49055 | - | - | int 16 | R
SD Card Connected | 47064 | - | - | int 16 | R | Overcurrent L2 | 51004 | 54004 | - | - | int 32 | R | Memory Read RGP | 49056 | - | - | int 16 | R
SD Card Removed | 47065 | - | - | int 16 | R | Overcurrent L3 | 51006 | 54006 | - | - | int 32 | R | Memory Read MinMax | 49057 | - | - | int 16 | R
SD Card Recording Started | 47066 | - | - | int 16 | R | Low Voltage L1 | 51008 | 54008 | - | - | int 32 | R | Memory Read AlarmList | 49060 | - | - | int 16 | R
SD Card Recording Ended | 47067 | - | - | int 16 | R | Low Voltage L2 | 51010 | 54010 | - | - | int 32 | R | SMPS Overvoltage | 49065 | - | - | int 16 | R
USB Connected | 47068 | - | - | int 16 | R | Low Voltage L3 | 51012 | 54012 | - | - | int 32 | R | SMPS Undervoltage | 49066 | - | - | int 16 | R
USB Removed | 47069 | - | - | int 16 | R | Overvoltage L1 | 51014 | 54014 | - | - | int 32 | R | Modbus_A DMA Timeout | 49067 | - | - | int 16 | R
USB Recording Started | 47070 | - | - | int 16 | R | Overvoltage L2 | 51016 | 54016 | - | - | int 32 | R | DMAA Uncleared Bit Error 485 | 49069 | - | - | int 16 | R
USB Recording Ended | 47071 | - | - | int 16 | R | Overvoltage L3 | 51018 | 54018 | - | - | int 32 | R | MB_A Parity Error | 49074 | - | - | int 16 | R
[6 empty] | Over-Inductive | 51020 | 54020 | - | - | int 32 | R | MB_A Noise Error | 49075 | - | - | int 16 | R
Events (Date of Occurrence) | [5 empty] | Over-Capacitive | 51022 | 54022 | - | - | int 32 | R | MB_A Frame Error | 49076 | - | - | int 16 | R
Alarm Name | Last Time Adress | First Time Adress | Multiplier | Unit | Data Type | C.T. Ratio Error | 51024 | 54024 | - | - | int 32 | R | MB_A Overrun Error | 49077 | - | - | int 16 | R
Low Voltage L1 | 50000 | 53000 | - | Timestamp | int 32 | C.T. Direction Changed | 51026 | 54026 | - | - | int 32 | R | MB_A Circular Buffer Full | 49078 | - | - | int 16 | R
Low Voltage L2 | 50002 | 53002 | - | Timestamp | int 32 | Automatic Installation | 51028 | 54028 | - | - | int 32 | R
Low Voltage L3 | 50004 | 53004 | - | Timestamp | int 32 | Current-Voltage Mismatch | 51030 | 54030 | - | - | int 32 | R
Missing Phase Terminal | 50006 | 53006 | - | Timestamp | int 32 | RTC Error | 51032 | 54032 | - | - | int 32 | R
No Voltage L1 | 50008 | 53008 | - | Timestamp | int 32 | SD Card Full | 51034 | 54034 | - | - | int 32 | R
No Voltage L2 | 50010 | 53010 | - | Timestamp | int 32 | SD Card Failed | 51036 | 54036 | - | - | int 32 | R
No Voltage L3 | 50012 | 53012 | - | Timestamp | int 32 | USB Memory Full | 51038 | 54038 | - | - | int 32 | R
Energies Cleared | 50014 | 53014 | - | Timestamp | int 32 | USB Failed | 51040 | 54040 | - | - | int 32 | R
Min Max Cleared | 50016 | 53016 | - | Timestamp | int 32 | USB Initialization Error | 51042 | 54042 | - | - | int 32 | R
Demands Cleared | 50018 | 53018 | - | Timestamp | int 32 | Pulse Index Value Low | 51044 | 54044 | - | - | int 32 | R
Device Powered On | 50040 | 53040 | - | Timestamp | int 32 | Over-Harmonic | 51046 | 54046 | - | - | int 32 | R
Device Powered Off | 50042 | 53042 | - | Timestamp | int 32 | Over-Harmonic L1 | 51048 | 54048 | - | - | int 32 | R
Date/Time Updated | 50044 | 53044 | - | Timestamp | int 32 | Over-Harmonic L2 | 51050 | 54050 | - | - | int 32 | R
Date/Time Changed | 50046 | 53046 | - | Timestamp | int 32 | Over-Harmonic L3 | 51052 | 54052 | - | - | int 32 | R
Date/Time Changed Remotely | 50048 | 53048 | - | Timestamp | int 32 | Overtemperature | 51054 | 54054 | - | - | int 32 | R
Language Changed | 50050 | 53050 | - | Timestamp | int 32 | Modbus Access Denied | 51056 | 54056 | - | - | int 32 | R
Pulse Output Counter Reset | 50072 | 53072 | - | Timestamp | int 32 | RGP Table Full | 51058 | 54058 | - | - | int 32 | R
Input-1 Trigger Counter Reset | 50074 | 53074 | - | Timestamp | int 32 | RTC Recovered | 51060 | 54060 | - | - | int 32 | R
Input-1 Pulse Counter Reset | 50076 | 53076 | - | Timestamp | int 32 | C.T. Ratio Changed | 51062 | 54062 | - | - | int 32 | R
Input-2 Trigger Counter Reset | 50078 | 53078 | - | Timestamp | int 32 | V.T. Ratio Changed | 51064 | 54064 | - | - | int 32 | R
Input-2 Pulse Counter Reset | 50080 | 53080 | - | Timestamp | int 32
Modbus Parity Error | 50082 | 53082 | - | Timestamp | int 32

## Commands
Adress | Command |  | W/R
9000 | Device Status
9001 | Clear Energies | 0xAA55 | 43605
9002 | Clear Min Max Values | 0xAA55 | 43605
9003 | Clear Demands | 0xAA55 | 43605
9004 | Clear All Alarms | 0xAA55 | 43605
9005 | Clear RGP | 0xAA55 | 43605
9022 | System Password Reset | 0xAA55 | 43605
9023 | Reserved (Dummy)
9024 | Restore Factory Settings | 0xAA55 | 43605
9025 | Device Reset | 0xAA55 | 43605
9026 | SD Card Start Recording | 0xAA55 | 43605
9027 | SD Card Stop Recording | 0xAA55 | 43605
9028 | SD Card Clear All Records | 0xAA55 | 43605
9029 | SD Card Format | 0xAA55 | 43605
9030 | SD Card Detect | 0xAA55 | 43605
9031 | SD Card Eject | 0xAA55 | 43605
9032 | SD Card Cancel Scheduled Recording | 0xAA56 | 43605
9033 | USB Start Recording | 0xAA55 | 43605
9034 | USB Stop Recording | 0xAA55 | 43605
9035 | USB Clear All Records | 0xAA55 | 43605
9036 | USB Format | 0xAA55 | 43605
9037 | USB Detect | 0xAA55 | 43605
9038 | USB Remove | 0xAA55 | 43605
9039 | USB Cancel Scheduled Recording | 0xAA56 | 43605
9040 | Clear Events | 0xAA55 | 43605
9041 | Clear Warnings | 0xAA55 | 43605
9049 | Reset Pulse Output Counter | 0xAA55 | 43605
9050 | Reset Input-1 Edge Trigger Counter | 0xAA55 | 43605
9051 | Reset Input-1 Pulse Counter | 0xAA55 | 43605
9052 | Reset Input-2 Edge Trigger Counter | 0xAA55 | 43605
9053 | Reset Input-2 Pulse Counter | 0xAA55 | 43605

## RGP
Sort by Duration | [5 empty] | Sort by Energy
Parameter Name | Adress | Multiplier | Unit | Data Type | W/R | Parameter Name | Adress | Multiplier | Unit | Data Type | W/R
RGP Number of Samples | 42000 | 1 | - | int 32 | R | RGP Number of Samples | 45000 | 1 | - | int 32 | R
RGP Power Resolution | 42002 | 1 | VAr | int 32 | R | RGP Power Resolution | 45002 | 1 | VAr | int 32 | R
RGP Difference Percentage | 42004 | 1 | % | int 32 | R | RGP Difference Percentage | 45004 | 1 | % | int 32 | R
RGP Maximum Difference Percentage | 42006 | 1 | % | int 32 | R | RGP Maximum Difference Percentage | 45006 | 1 | % | int 32 | R
RGP Instant Duration | 42008 | 0.1 | % | int 32 | R | RGP Instant Duration | 45008 | 0.1 | % | int 32 | R
RGP Instant Q1 | 42010 | 0.001 | VAr | int 32 | R | RGP Instant Q1 | 45010 | 0.001 | VAr | int 32 | R
RGP Instant Q2 | 42012 | 0.001 | VAr | int 32 | R | RGP Instant Q2 | 45012 | 0.001 | VAr | int 32 | R
RGP Instant Q3 | 42014 | 0.001 | VAr | int 32 | R | RGP Instant Q3 | 45014 | 0.001 | VAr | int 32 | R
RGP 1 Duration | 42016 | 0.1 | % | int 32 | R | RGP 1 Süre | 45016 | 0.1 | % | int 32 | R
RGP 1 Q1 | 42018 | 0.001 | VAr | int 32 | R | RGP 1 Q1 | 45018 | 0.001 | VAr | int 32 | R
RGP 1 Q2 | 42020 | 0.001 | VAr | int 32 | R | RGP 1 Q2 | 45020 | 0.001 | VAr | int 32 | R
RGP 1 Q3 | 42022 | 0.001 | VAr | int 32 | R | RGP 1 Q3 | 45022 | 0.001 | VAr | int 32 | R
RGP 2 Duration | 42024 | 0.1 | % | int 32 | R | RGP 2 Duration | 45024 | 0.1 | % | int 32 | R
RGP 2 Q1 | 42026 | 0.001 | VAr | int 32 | R | RGP 2 Q1 | 45026 | 0.001 | VAr | int 32 | R
RGP 2 Q2 | 42028 | 0.001 | VAr | int 32 | R | RGP 2 Q2 | 45028 | 0.001 | VAr | int 32 | R
RGP 2 Q3 | 42030 | 0.001 | VAr | int 32 | R | RGP 2 Q3 | 45030 | 0.001 | VAr | int 32 | R
RGP 3 Duration | 42032 | 0.1 | % | int 32 | R | RGP 3 Duration | 45032 | 0.1 | % | int 32 | R
RGP 3 Q1 | 42034 | 0.001 | VAr | int 32 | R | RGP 3 Q1 | 45034 | 0.001 | VAr | int 32 | R
RGP 3 Q2 | 42036 | 0.001 | VAr | int 32 | R | RGP 3 Q2 | 45036 | 0.001 | VAr | int 32 | R
RGP 3 Q3 | 42038 | 0.001 | VAr | int 32 | R | RGP 3 Q3 | 45038 | 0.001 | VAr | int 32 | R
RGP 4 Duration | 42040 | 0.1 | % | int 32 | R | RGP 4 Duration | 45040 | 0.1 | % | int 32 | R
RGP 4 Q1 | 42042 | 0.001 | VAr | int 32 | R | RGP 4 Q1 | 45042 | 0.001 | VAr | int 32 | R
RGP 4 Q2 | 42044 | 0.001 | VAr | int 32 | R | RGP 4 Q2 | 45044 | 0.001 | VAr | int 32 | R
RGP 4 Q3 | 42046 | 0.001 | VAr | int 32 | R | RGP 4 Q3 | 45046 | 0.001 | VAr | int 32 | R
RGP 5 Duration | 42048 | 0.1 | % | int 32 | R | RGP 5 Duration | 45048 | 0.1 | % | int 32 | R
RGP 5 Q1 | 42050 | 0.001 | VAr | int 32 | R | RGP 5 Q1 | 45050 | 0.001 | VAr | int 32 | R
RGP 5 Q2 | 42052 | 0.001 | VAr | int 32 | R | RGP 5 Q2 | 45052 | 0.001 | VAr | int 32 | R
RGP 5 Q3 | 42054 | 0.001 | VAr | int 32 | R | RGP 5 Q3 | 45054 | 0.001 | VAr | int 32 | R
RGP 6 Duration | 42056 | 0.1 | % | int 32 | R | RGP 6 Duration | 45056 | 0.1 | % | int 32 | R
RGP 6 Q1 | 42058 | 0.001 | VAr | int 32 | R | RGP 6 Q1 | 45058 | 0.001 | VAr | int 32 | R
RGP 6 Q2 | 42060 | 0.001 | VAr | int 32 | R | RGP 6 Q2 | 45060 | 0.001 | VAr | int 32 | R
RGP 6 Q3 | 42062 | 0.001 | VAr | int 32 | R | RGP 6 Q3 | 45062 | 0.001 | VAr | int 32 | R
RGP 7 Duration | 42064 | 0.1 | % | int 32 | R | RGP 7 Duration | 45064 | 0.1 | % | int 32 | R
RGP 7 Q1 | 42066 | 0.001 | VAr | int 32 | R | RGP 7 Q1 | 45066 | 0.001 | VAr | int 32 | R
RGP 7 Q2 | 42068 | 0.001 | VAr | int 32 | R | RGP 7 Q2 | 45068 | 0.001 | VAr | int 32 | R
RGP 7 Q3 | 42070 | 0.001 | VAr | int 32 | R | RGP 7 Q3 | 45070 | 0.001 | VAr | int 32 | R
RGP 8 Duration | 42072 | 0.1 | % | int 32 | R | RGP 8 Duration | 45072 | 0.1 | % | int 32 | R
RGP 8 Q1 | 42074 | 0.001 | VAr | int 32 | R | RGP 8 Q1 | 45074 | 0.001 | VAr | int 32 | R
RGP 8 Q2 | 42076 | 0.001 | VAr | int 32 | R | RGP 8 Q2 | 45076 | 0.001 | VAr | int 32 | R
RGP 8 Q3 | 42078 | 0.001 | VAr | int 32 | R | RGP 8 Q3 | 45078 | 0.001 | VAr | int 32 | R
RGP 9 Duration | 42080 | 0.1 | % | int 32 | R | RGP 9 Duration | 45080 | 0.1 | % | int 32 | R
RGP 9 Q1 | 42082 | 0.001 | VAr | int 32 | R | RGP 9 Q1 | 45082 | 0.001 | VAr | int 32 | R
RGP 9 Q2 | 42084 | 0.001 | VAr | int 32 | R | RGP 9 Q2 | 45084 | 0.001 | VAr | int 32 | R
RGP 9 Q3 | 42086 | 0.001 | VAr | int 32 | R | RGP 9 Q3 | 45086 | 0.001 | VAr | int 32 | R
RGP 10 Süre | 42088 | 0.1 | % | int 32 | R | RGP 10 Duration | 45088 | 0.1 | % | int 32 | R
RGP 10 Q1 | 42090 | 0.001 | VAr | int 32 | R | RGP 10 Q1 | 45090 | 0.001 | VAr | int 32 | R
RGP 10 Q2 | 42092 | 0.001 | VAr | int 32 | R | RGP 10 Q2 | 45092 | 0.001 | VAr | int 32 | R
RGP 10 Q3 | 42094 | 0.001 | VAr | int 32 | R | RGP 10 Q3 | 45094 | 0.001 | VAr | int 32 | R
RGP 11 Duration | 42096 | 0.1 | % | int 32 | R | RGP 11 Duration | 45096 | 0.1 | % | int 32 | R
RGP 11 Q1 | 42098 | 0.001 | VAr | int 32 | R | RGP 11 Q1 | 45098 | 0.001 | VAr | int 32 | R
RGP 11 Q2 | 42100 | 0.001 | VAr | int 32 | R | RGP 11 Q2 | 45100 | 0.001 | VAr | int 32 | R
RGP 11 Q3 | 42102 | 0.001 | VAr | int 32 | R | RGP 11 Q3 | 45102 | 0.001 | VAr | int 32 | R
RGP 12 Duration | 42104 | 0.1 | % | int 32 | R | RGP 12 Duration | 45104 | 0.1 | % | int 32 | R
RGP 12 Q1 | 42106 | 0.001 | VAr | int 32 | R | RGP 12 Q1 | 45106 | 0.001 | VAr | int 32 | R
RGP 12 Q2 | 42108 | 0.001 | VAr | int 32 | R | RGP 12 Q2 | 45108 | 0.001 | VAr | int 32 | R
RGP 12 Q3 | 42110 | 0.001 | VAr | int 32 | R | RGP 12 Q3 | 45110 | 0.001 | VAr | int 32 | R
RGP 13 Duration | 42112 | 0.1 | % | int 32 | R | RGP 13 Duration | 45112 | 0.1 | % | int 32 | R
RGP 13 Q1 | 42114 | 0.001 | VAr | int 32 | R | RGP 13 Q1 | 45114 | 0.001 | VAr | int 32 | R
RGP 13 Q2 | 42116 | 0.001 | VAr | int 32 | R | RGP 13 Q2 | 45116 | 0.001 | VAr | int 32 | R
RGP 13 Q3 | 42118 | 0.001 | VAr | int 32 | R | RGP 13 Q3 | 45118 | 0.001 | VAr | int 32 | R
RGP 14 Duration | 42120 | 0.1 | % | int 32 | R | RGP 14 Duration | 45120 | 0.1 | % | int 32 | R
RGP 14 Q1 | 42122 | 0.001 | VAr | int 32 | R | RGP 14 Q1 | 45122 | 0.001 | VAr | int 32 | R
RGP 14 Q2 | 42124 | 0.001 | VAr | int 32 | R | RGP 14 Q2 | 45124 | 0.001 | VAr | int 32 | R
RGP 14 Q3 | 42126 | 0.001 | VAr | int 32 | R | RGP 14 Q3 | 45126 | 0.001 | VAr | int 32 | R
RGP 15 Duration | 42128 | 0.1 | % | int 32 | R | RGP 15 Duration | 45128 | 0.1 | % | int 32 | R
RGP 15 Q1 | 42130 | 0.001 | VAr | int 32 | R | RGP 15 Q1 | 45130 | 0.001 | VAr | int 32 | R
RGP 15 Q2 | 42132 | 0.001 | VAr | int 32 | R | RGP 15 Q2 | 45132 | 0.001 | VAr | int 32 | R
RGP 15 Q3 | 42134 | 0.001 | VAr | int 32 | R | RGP 15 Q3 | 45134 | 0.001 | VAr | int 32 | R
RGP 16 Süre | 42136 | 0.1 | % | int 32 | R | RGP 16 Süre | 45136 | 0.1 | % | int 32 | R
RGP 17 Q1 | 42138 | 0.001 | VAr | int 32 | R | RGP 17 Q1 | 45138 | 0.001 | VAr | int 32 | R
RGP 17 Q2 | 42140 | 0.001 | VAr | int 32 | R | RGP 17 Q2 | 45140 | 0.001 | VAr | int 32 | R
RGP 17 Q3 | 42142 | 0.001 | VAr | int 32 | R | RGP 17 Q3 | 45142 | 0.001 | VAr | int 32 | R
RGP 18 Duration | 42144 | 0.1 | % | int 32 | R | RGP 18 Duration | 45144 | 0.1 | % | int 32 | R
RGP 18 Q1 | 42146 | 0.001 | VAr | int 32 | R | RGP 18 Q1 | 45146 | 0.001 | VAr | int 32 | R
RGP 18 Q2 | 42148 | 0.001 | VAr | int 32 | R | RGP 18 Q2 | 45148 | 0.001 | VAr | int 32 | R
RGP 18 Q3 | 42150 | 0.001 | VAr | int 32 | R | RGP 18 Q3 | 45150 | 0.001 | VAr | int 32 | R
RGP 19 Duration | 42152 | 0.1 | % | int 32 | R | RGP 19 Duration | 45152 | 0.1 | % | int 32 | R
RGP 19 Q1 | 42154 | 0.001 | VAr | int 32 | R | RGP 19 Q1 | 45154 | 0.001 | VAr | int 32 | R
RGP 19 Q2 | 42156 | 0.001 | VAr | int 32 | R | RGP 19 Q2 | 45156 | 0.001 | VAr | int 32 | R
RGP 19 Q3 | 42158 | 0.001 | VAr | int 32 | R | RGP 19 Q3 | 45158 | 0.001 | VAr | int 32 | R
RGP 20 Duration | 42160 | 0.1 | % | int 32 | R | RGP 20 Duration | 45160 | 0.1 | % | int 32 | R
RGP 20 Q1 | 42162 | 0.001 | VAr | int 32 | R | RGP 20 Q1 | 45162 | 0.001 | VAr | int 32 | R
RGP 20 Q2 | 42164 | 0.001 | VAr | int 32 | R | RGP 20 Q2 | 45164 | 0.001 | VAr | int 32 | R
RGP 20 Q3 | 42166 | 0.001 | VAr | int 32 | R | RGP 20 Q3 | 45166 | 0.001 | VAr | int 32 | R
Sort by Inductive | [5 empty] | Sort by Ratio
Parameter Name | Adress | Multiplier | Unit | Data Type | W/R | Parameter Name | Adress | Multiplier | Unit | Data Type | W/R
RGP Number of Samples | 43000 | 1 | - | int 32 | R | RGP Number of Samples | 46000 | 1 | - | int 32 | R
RGP Power Resolution | 43002 | 1 | VAr | int 32 | R | RGP Power Resolution | 46002 | 1 | VAr | int 32 | R
RGP Difference Percentage | 43004 | 1 | % | int 32 | R | RGP Difference Percentage | 46004 | 1 | % | int 32 | R
RGP Maximum Difference Percentage | 43006 | 1 | % | int 32 | R | RGP Maximum Difference Percentage | 46006 | 1 | % | int 32 | R
RGP Instant Duration | 43008 | 0.1 | % | int 32 | R | RGP Instant Duration | 46008 | 0.1 | % | int 32 | R
RGP Instant Q1 | 43010 | 0.001 | VAr | int 32 | R | RGP Instant Q1 | 46010 | 0.001 | VAr | int 32 | R
RGP Instant Q2 | 43012 | 0.001 | VAr | int 32 | R | RGP Instant Q2 | 46012 | 0.001 | VAr | int 32 | R
RGP Instant Q3 | 43014 | 0.001 | VAr | int 32 | R | RGP Instant Q3 | 46014 | 0.001 | VAr | int 32 | R
RGP 1 Duration | 43016 | 0.1 | % | int 32 | R | RGP 1 Duration | 46016 | 0.1 | % | int 32 | R
RGP 1 Q1 | 43018 | 0.001 | VAr | int 32 | R | RGP 1 Q1 | 46018 | 0.001 | VAr | int 32 | R
RGP 1 Q2 | 43020 | 0.001 | VAr | int 32 | R | RGP 1 Q2 | 46020 | 0.001 | VAr | int 32 | R
RGP 1 Q3 | 43022 | 0.001 | VAr | int 32 | R | RGP 1 Q3 | 46022 | 0.001 | VAr | int 32 | R
RGP 2 Duration | 43024 | 0.1 | % | int 32 | R | RGP 2 Duration | 46024 | 0.1 | % | int 32 | R
RGP 2 Q1 | 43026 | 0.001 | VAr | int 32 | R | RGP 2 Q1 | 46026 | 0.001 | VAr | int 32 | R
RGP 2 Q2 | 43028 | 0.001 | VAr | int 32 | R | RGP 2 Q2 | 46028 | 0.001 | VAr | int 32 | R
RGP 2 Q3 | 43030 | 0.001 | VAr | int 32 | R | RGP 2 Q3 | 46030 | 0.001 | VAr | int 32 | R
RGP 3 Duration | 43032 | 0.1 | % | int 32 | R | RGP 3 Duration | 46032 | 0.1 | % | int 32 | R
RGP 3 Q1 | 43034 | 0.001 | VAr | int 32 | R | RGP 3 Q1 | 46034 | 0.001 | VAr | int 32 | R
RGP 3 Q2 | 43036 | 0.001 | VAr | int 32 | R | RGP 3 Q2 | 46036 | 0.001 | VAr | int 32 | R
RGP 3 Q3 | 43038 | 0.001 | VAr | int 32 | R | RGP 3 Q3 | 46038 | 0.001 | VAr | int 32 | R
RGP 4 Duration | 43040 | 0.1 | % | int 32 | R | RGP 4 Duration | 46040 | 0.1 | % | int 32 | R
RGP 4 Q1 | 43042 | 0.001 | VAr | int 32 | R | RGP 4 Q1 | 46042 | 0.001 | VAr | int 32 | R
RGP 4 Q2 | 43044 | 0.001 | VAr | int 32 | R | RGP 4 Q2 | 46044 | 0.001 | VAr | int 32 | R
RGP 4 Q3 | 43046 | 0.001 | VAr | int 32 | R | RGP 4 Q3 | 46046 | 0.001 | VAr | int 32 | R
RGP 5 Duration | 43048 | 0.1 | % | int 32 | R | RGP 5 Duration | 46048 | 0.1 | % | int 32 | R
RGP 5 Q1 | 43050 | 0.001 | VAr | int 32 | R | RGP 5 Q1 | 46050 | 0.001 | VAr | int 32 | R
RGP 5 Q2 | 43052 | 0.001 | VAr | int 32 | R | RGP 5 Q2 | 46052 | 0.001 | VAr | int 32 | R
RGP 5 Q3 | 43054 | 0.001 | VAr | int 32 | R | RGP 5 Q3 | 46054 | 0.001 | VAr | int 32 | R
RGP 6 Duration | 43056 | 0.1 | % | int 32 | R | RGP 6 Duration | 46056 | 0.1 | % | int 32 | R
RGP 6 Q1 | 43058 | 0.001 | VAr | int 32 | R | RGP 6 Q1 | 46058 | 0.001 | VAr | int 32 | R
RGP 6 Q2 | 43060 | 0.001 | VAr | int 32 | R | RGP 6 Q2 | 46060 | 0.001 | VAr | int 32 | R
RGP 6 Q3 | 43062 | 0.001 | VAr | int 32 | R | RGP 6 Q3 | 46062 | 0.001 | VAr | int 32 | R
RGP 7 Duration | 43064 | 0.1 | % | int 32 | R | RGP 7 Duration | 46064 | 0.1 | % | int 32 | R
RGP 7 Q1 | 43066 | 0.001 | VAr | int 32 | R | RGP 7 Q1 | 46066 | 0.001 | VAr | int 32 | R
RGP 7 Q2 | 43068 | 0.001 | VAr | int 32 | R | RGP 7 Q2 | 46068 | 0.001 | VAr | int 32 | R
RGP 7 Q3 | 43070 | 0.001 | VAr | int 32 | R | RGP 7 Q3 | 46070 | 0.001 | VAr | int 32 | R
RGP 8 Duration | 43072 | 0.1 | % | int 32 | R | RGP 8 Duration | 46072 | 0.1 | % | int 32 | R
RGP 8 Q1 | 43074 | 0.001 | VAr | int 32 | R | RGP 8 Q1 | 46074 | 0.001 | VAr | int 32 | R
RGP 8 Q2 | 43076 | 0.001 | VAr | int 32 | R | RGP 8 Q2 | 46076 | 0.001 | VAr | int 32 | R
RGP 8 Q3 | 43078 | 0.001 | VAr | int 32 | R | RGP 8 Q3 | 46078 | 0.001 | VAr | int 32 | R
RGP 9 Duration | 43080 | 0.1 | % | int 32 | R | RGP 9 Duration | 46080 | 0.1 | % | int 32 | R
RGP 9 Q1 | 43082 | 0.001 | VAr | int 32 | R | RGP 9 Q1 | 46082 | 0.001 | VAr | int 32 | R
RGP 9 Q2 | 43084 | 0.001 | VAr | int 32 | R | RGP 9 Q2 | 46084 | 0.001 | VAr | int 32 | R
RGP 9 Q3 | 43086 | 0.001 | VAr | int 32 | R | RGP 9 Q3 | 46086 | 0.001 | VAr | int 32 | R
RGP 10 Süre | 43088 | 0.1 | % | int 32 | R | RGP 10 Süre | 46088 | 0.1 | % | int 32 | R
RGP 10 Q1 | 43090 | 0.001 | VAr | int 32 | R | RGP 10 Q1 | 46090 | 0.001 | VAr | int 32 | R
RGP 10 Q2 | 43092 | 0.001 | VAr | int 32 | R | RGP 10 Q2 | 46092 | 0.001 | VAr | int 32 | R
RGP 10 Q3 | 43094 | 0.001 | VAr | int 32 | R | RGP 10 Q3 | 46094 | 0.001 | VAr | int 32 | R
RGP 11 Duration | 43096 | 0.1 | % | int 32 | R | RGP 11 Duration | 46096 | 0.1 | % | int 32 | R
RGP 11 Q1 | 43098 | 0.001 | VAr | int 32 | R | RGP 11 Q1 | 46098 | 0.001 | VAr | int 32 | R
RGP 11 Q2 | 43100 | 0.001 | VAr | int 32 | R | RGP 11 Q2 | 46100 | 0.001 | VAr | int 32 | R
RGP 11 Q3 | 43102 | 0.001 | VAr | int 32 | R | RGP 11 Q3 | 46102 | 0.001 | VAr | int 32 | R
RGP 12 Duration | 43104 | 0.1 | % | int 32 | R | RGP 12 Duration | 46104 | 0.1 | % | int 32 | R
RGP 12 Q1 | 43106 | 0.001 | VAr | int 32 | R | RGP 12 Q1 | 46106 | 0.001 | VAr | int 32 | R
RGP 12 Q2 | 43108 | 0.001 | VAr | int 32 | R | RGP 12 Q2 | 46108 | 0.001 | VAr | int 32 | R
RGP 12 Q3 | 43110 | 0.001 | VAr | int 32 | R | RGP 12 Q3 | 46110 | 0.001 | VAr | int 32 | R
RGP 13 Duration | 43112 | 0.1 | % | int 32 | R | RGP 13 Duration | 46112 | 0.1 | % | int 32 | R
RGP 13 Q1 | 43114 | 0.001 | VAr | int 32 | R | RGP 13 Q1 | 46114 | 0.001 | VAr | int 32 | R
RGP 13 Q2 | 43116 | 0.001 | VAr | int 32 | R | RGP 13 Q2 | 46116 | 0.001 | VAr | int 32 | R
RGP 13 Q3 | 43118 | 0.001 | VAr | int 32 | R | RGP 13 Q3 | 46118 | 0.001 | VAr | int 32 | R
RGP 14 Duration | 43120 | 0.1 | % | int 32 | R | RGP 14 Duration | 46120 | 0.1 | % | int 32 | R
RGP 14 Q1 | 43122 | 0.001 | VAr | int 32 | R | RGP 14 Q1 | 46122 | 0.001 | VAr | int 32 | R
RGP 14 Q2 | 43124 | 0.001 | VAr | int 32 | R | RGP 14 Q2 | 46124 | 0.001 | VAr | int 32 | R
RGP 14 Q3 | 43126 | 0.001 | VAr | int 32 | R | RGP 14 Q3 | 46126 | 0.001 | VAr | int 32 | R
RGP 15 Duration | 43128 | 0.1 | % | int 32 | R | RGP 15 Duration | 46128 | 0.1 | % | int 32 | R
RGP 15 Q1 | 43130 | 0.001 | VAr | int 32 | R | RGP 15 Q1 | 46130 | 0.001 | VAr | int 32 | R
RGP 15 Q2 | 43132 | 0.001 | VAr | int 32 | R | RGP 15 Q2 | 46132 | 0.001 | VAr | int 32 | R
RGP 15 Q3 | 43134 | 0.001 | VAr | int 32 | R | RGP 15 Q3 | 46134 | 0.001 | VAr | int 32 | R
RGP 16 Süre | 43136 | 0.1 | % | int 32 | R | RGP 16 Süre | 46136 | 0.1 | % | int 32 | R
RGP 17 Q1 | 43138 | 0.001 | VAr | int 32 | R | RGP 17 Q1 | 46138 | 0.001 | VAr | int 32 | R
RGP 17 Q2 | 43140 | 0.001 | VAr | int 32 | R | RGP 17 Q2 | 46140 | 0.001 | VAr | int 32 | R
RGP 17 Q3 | 43142 | 0.001 | VAr | int 32 | R | RGP 17 Q3 | 46142 | 0.001 | VAr | int 32 | R
RGP 18 Duration | 43144 | 0.1 | % | int 32 | R | RGP 18 Duration | 46144 | 0.1 | % | int 32 | R
RGP 18 Q1 | 43146 | 0.001 | VAr | int 32 | R | RGP 18 Q1 | 46146 | 0.001 | VAr | int 32 | R
RGP 18 Q2 | 43148 | 0.001 | VAr | int 32 | R | RGP 18 Q2 | 46148 | 0.001 | VAr | int 32 | R
RGP 18 Q3 | 43150 | 0.001 | VAr | int 32 | R | RGP 18 Q3 | 46150 | 0.001 | VAr | int 32 | R
RGP 19 Duration | 43152 | 0.1 | % | int 32 | R | RGP 19 Duration | 46152 | 0.1 | % | int 32 | R
RGP 19 Q1 | 43154 | 0.001 | VAr | int 32 | R | RGP 19 Q1 | 46154 | 0.001 | VAr | int 32 | R
RGP 19 Q2 | 43156 | 0.001 | VAr | int 32 | R | RGP 19 Q2 | 46156 | 0.001 | VAr | int 32 | R
RGP 19 Q3 | 43158 | 0.001 | VAr | int 32 | R | RGP 19 Q3 | 46158 | 0.001 | VAr | int 32 | R
RGP 20 Duration | 43160 | 0.1 | % | int 32 | R | RGP 20 Duration | 46160 | 0.1 | % | int 32 | R
RGP 20 Q1 | 43162 | 0.001 | VAr | int 32 | R | RGP 20 Q1 | 46162 | 0.001 | VAr | int 32 | R
RGP 20 Q2 | 43164 | 0.001 | VAr | int 32 | R | RGP 20 Q2 | 46164 | 0.001 | VAr | int 32 | R
RGP 20 Q3 | 43166 | 0.001 | VAr | int 32 | R | RGP 20 Q3 | 46166 | 0.001 | VAr | int 32 | R
KAPASİTİFE GÖRE SIRALANMIŞ
PARAMETRE ADI | ADRES | ÇARPAN | BİRİM | DATA TİPİ | W/R
RGP Number of Samples | 44000 | 1 | - | int 32 | R
RGP Power Resolution | 44002 | 1 | VAr | int 32 | R
RGP Difference Percentage | 44004 | 1 | % | int 32 | R
RGP Maximum Difference Percentage | 44006 | 1 | % | int 32 | R
RGP Instant Duration | 44008 | 0.1 | % | int 32 | R
RGP Instant Q1 | 44010 | 0.001 | VAr | int 32 | R
RGP Instant Q2 | 44012 | 0.001 | VAr | int 32 | R
RGP Instant Q3 | 44014 | 0.001 | VAr | int 32 | R
RGP 1 Duration | 44016 | 0.1 | % | int 32 | R
RGP 1 Q1 | 44018 | 0.001 | VAr | int 32 | R
RGP 1 Q2 | 44020 | 0.001 | VAr | int 32 | R
RGP 1 Q3 | 44022 | 0.001 | VAr | int 32 | R
RGP 2 Duration | 44024 | 0.1 | % | int 32 | R
RGP 2 Q1 | 44026 | 0.001 | VAr | int 32 | R
RGP 2 Q2 | 44028 | 0.001 | VAr | int 32 | R
RGP 2 Q3 | 44030 | 0.001 | VAr | int 32 | R
RGP 3 Duration | 44032 | 0.1 | % | int 32 | R
RGP 3 Q1 | 44034 | 0.001 | VAr | int 32 | R
RGP 3 Q2 | 44036 | 0.001 | VAr | int 32 | R
RGP 3 Q3 | 44038 | 0.001 | VAr | int 32 | R
RGP 4 Duration | 44040 | 0.1 | % | int 32 | R
RGP 4 Q1 | 44042 | 0.001 | VAr | int 32 | R
RGP 4 Q2 | 44044 | 0.001 | VAr | int 32 | R
RGP 4 Q3 | 44046 | 0.001 | VAr | int 32 | R
RGP 5 Duration | 44048 | 0.1 | % | int 32 | R
RGP 5 Q1 | 44050 | 0.001 | VAr | int 32 | R
RGP 5 Q2 | 44052 | 0.001 | VAr | int 32 | R
RGP 5 Q3 | 44054 | 0.001 | VAr | int 32 | R
RGP 6 Duration | 44056 | 0.1 | % | int 32 | R
RGP 6 Q1 | 44058 | 0.001 | VAr | int 32 | R
RGP 6 Q2 | 44060 | 0.001 | VAr | int 32 | R
RGP 6 Q3 | 44062 | 0.001 | VAr | int 32 | R
RGP 7 Duration | 44064 | 0.1 | % | int 32 | R
RGP 7 Q1 | 44066 | 0.001 | VAr | int 32 | R
RGP 7 Q2 | 44068 | 0.001 | VAr | int 32 | R
RGP 7 Q3 | 44070 | 0.001 | VAr | int 32 | R
RGP 8 Duration | 44072 | 0.1 | % | int 32 | R
RGP 8 Q1 | 44074 | 0.001 | VAr | int 32 | R
RGP 8 Q2 | 44076 | 0.001 | VAr | int 32 | R
RGP 8 Q3 | 44078 | 0.001 | VAr | int 32 | R
RGP 9 Duration | 44080 | 0.1 | % | int 32 | R
RGP 9 Q1 | 44082 | 0.001 | VAr | int 32 | R
RGP 9 Q2 | 44084 | 0.001 | VAr | int 32 | R
RGP 9 Q3 | 44086 | 0.001 | VAr | int 32 | R
RGP 10 Süre | 44088 | 0.1 | % | int 32 | R
RGP 10 Q1 | 44090 | 0.001 | VAr | int 32 | R
RGP 10 Q2 | 44092 | 0.001 | VAr | int 32 | R
RGP 10 Q3 | 44094 | 0.001 | VAr | int 32 | R
RGP 11 Duration | 44096 | 0.1 | % | int 32 | R
RGP 11 Q1 | 44098 | 0.001 | VAr | int 32 | R
RGP 11 Q2 | 44100 | 0.001 | VAr | int 32 | R
RGP 11 Q3 | 44102 | 0.001 | VAr | int 32 | R
RGP 12 Duration | 44104 | 0.1 | % | int 32 | R
RGP 12 Q1 | 44106 | 0.001 | VAr | int 32 | R
RGP 12 Q2 | 44108 | 0.001 | VAr | int 32 | R
RGP 12 Q3 | 44110 | 0.001 | VAr | int 32 | R
RGP 13 Duration | 44112 | 0.1 | % | int 32 | R
RGP 13 Q1 | 44114 | 0.001 | VAr | int 32 | R
RGP 13 Q2 | 44116 | 0.001 | VAr | int 32 | R
RGP 13 Q3 | 44118 | 0.001 | VAr | int 32 | R
RGP 14 Duration | 44120 | 0.1 | % | int 32 | R
RGP 14 Q1 | 44122 | 0.001 | VAr | int 32 | R
RGP 14 Q2 | 44124 | 0.001 | VAr | int 32 | R
RGP 14 Q3 | 44126 | 0.001 | VAr | int 32 | R
RGP 15 Duration | 44128 | 0.1 | % | int 32 | R
RGP 15 Q1 | 44130 | 0.001 | VAr | int 32 | R
RGP 15 Q2 | 44132 | 0.001 | VAr | int 32 | R
RGP 15 Q3 | 44134 | 0.001 | VAr | int 32 | R
RGP 16 Süre | 44136 | 0.1 | % | int 32 | R
RGP 17 Q1 | 44138 | 0.001 | VAr | int 32 | R
RGP 17 Q2 | 44140 | 0.001 | VAr | int 32 | R
RGP 17 Q3 | 44142 | 0.001 | VAr | int 32 | R
RGP 18 Duration | 44144 | 0.1 | % | int 32 | R
RGP 18 Q1 | 44146 | 0.001 | VAr | int 32 | R
RGP 18 Q2 | 44148 | 0.001 | VAr | int 32 | R
RGP 18 Q3 | 44150 | 0.001 | VAr | int 32 | R
RGP 19 Duration | 44152 | 0.1 | % | int 32 | R
RGP 19 Q1 | 44154 | 0.001 | VAr | int 32 | R
RGP 19 Q2 | 44156 | 0.001 | VAr | int 32 | R
RGP 19 Q3 | 44158 | 0.001 | VAr | int 32 | R
RGP 20 Duration | 44160 | 0.1 | % | int 32 | R
RGP 20 Q1 | 44162 | 0.001 | VAr | int 32 | R
RGP 20 Q2 | 44164 | 0.001 | VAr | int 32 | R
RGP 20 Q3 | 44166 | 0.001 | VAr | int 32 | R